## Acknowledgements
Date: 22/06/2022
Authors: Matthew Emes, Azadeh Jafari, Maziar Arjomandi, Mike Collins
Version: 1C
Note
This spreadsheet contains unpublished data from the work of the University of Adelaide School of Mechanical Engineering, through the Australian Solar Thermal Research Initiative (ASTRI). This data should not be distributed to other parties without permission from University of Adelaide.
Important disclaimer
ASTRI advises that the information contained in this publication comprises general statements based on scientific research. The reader is advised and needs to be aware that such information may be incomplete or unable to be used in any specific situation. No reliance or actions must therefore be made on that information without seeking prior expert professional, scientific and technical advice. To the extent permitted by law, ASTRI (including its employees and consultants) excludes all liability to any person for any consequences, including but not limited to all losses, damages, costs, expenses and any other compensation, arising directly or indirectly from using this publication (in part or in whole) and any information or material contained in it.
The Australian Solar Thermal Research Initiative (ASTRI) Program is supported by the Australian Government through the Australian Renewable Energy Agency (ARENA)
For Further Information
Matthew Emes t +61 4 3277 1245 e matthew.emes@adelaide.edu.au
Azadeh Jafari t +61 4 2414 9290 e azadeh.jafari@adelaide.edu.au
Maziar Arjomandi t +61 4 0066 9063 e maziar.arjomandi@adelaide.edu.au
Mike Collins t +61 4 3118 4676 e mike.collins@csiro.au

## Heliostat Coordinate System
Definitions
α | Elevation angle (°)
β | Azimuth angle (°)
U | Mean wind speed (m/s)
l_px | Centre of pressure distance (m)
c | Heliostat mirror chord length (m)
H | Heliostat elevation axis height (m)
Load coefficients
CFx = Fx/(1/2ρU2A) | Drag force coefficient
CFz = Fz/(1/2ρU2A) | Lift force coefficient
CMHx = MHx/(1/2ρU2Ac) | Hinge moment about x_H axis
CMHy = MHy/(1/2ρU2Ac) | Hinge moment about y_H azis
CMy = My/(1/2ρU2AH) | Overturning moment about y_b axis at heliostat base
CMz = Mz/(1/2ρU2Ac) | Azimuth moment about z axis
Velocity and turbulence characteristics
z_0 | Log law roughness parameter (m)
α | Power law velocity profile exponent
I_u = U_rms/U_mean | Turbulence intensity (%)
G_u = U_gust/U_mean | Gust factor
Effect of terrain on ABL velocity profiles (Peterka and Derickson 1992) |  |  | Turbulence intensity profiles (ESDU 85020, 2001) | Gust factor profiles (ESDU 85020, 2001) | Gust factor profiles (ESDU 85020, 2001)
Terrain description | z_0 (m) | α
Open country with isolated trees and buildings | 0.03 | 0.17
Grass and very few trees | 0.01 | 0.15
Flat desert | 0.003 | 0.12

## Mean and Peak Coefficients
Mean drag coefficients | cFx | β (°) | [6 empty] | Mean drag coefficients | cFx | β (°)
c = 0.8 m | α (°) | 0 | 30 | 60 | 90 | 120 | 150 | 180 | c = 0.8 m | α (°) | 0 | 30 | 60 | 90 | 120 | 150 | 180
H = 0.5 m | 0 | 0.082906 | 0.074398 | 0.053181 | 0.095626 | -0.063765 | -0.06414 | -0.058963 | H = 0.5 m | 0 | 0.097491 | 0.071066 | 0.12939 | 0.13096 | -0.088897 | -0.085757 | -0.08458
U = 8.4 m/s | 15 | 0.18997 | 0.16657 | 0.11007 | 0.016678 | -0.091878 | -0.14272 | -0.1519 | U = 6 m/s | 15 | 0.46195 | 0.15177 | 0.23472 | 0.015731 | -0.087624 | -0.1389 | -0.16965
I_u = 13% | 30 | 0.89279 | 0.75456 | 0.45333 | 0.024266 | -0.37953 | -0.67219 | -0.6873 | I_u = 26% | 30 | 1.0996 | 0.78866 | 0.37656 | 0.047927 | -0.47527 | -0.97229 | -0.86689
G_u = 1.44 | 45 | 1.2171 | 1.1979 | 0.87338 | 0.10094 | -0.90931 | -1.0404 | -0.96312 | G_u = 1.70 | 45 | 1.6228 | 1.348 | 1.1885 | 0.078453 | -0.9996 | -1.5774 | -1.2296
| 60 | 1.3991 | 1.3622 | 1.173 | 0.024495 | -1.0957 | -1.1258 | -1.2395 |  | 60 | 2.0737 | 1.7788 | 1.4903 | 0.025239 | -1.4156 | -1.4581 | -1.902
| 75 | 1.4858 | 1.4096 | 1.3172 | 0.13709 | -1.199 | -1.3465 | -1.3417 |  | 75 | 2.1314 | 2.0484 | 1.7811 | 0.053662 | -2.0695 | -1.7228 | -2.0236
| 90 | 1.5119 | 1.4146 | 1.365 | 0.049868 | -1.2987 | -1.4361 | -1.4956 |  | 90 | 2.1611 | 1.9857 | 1.8624 | -0.33044 | -1.8943 | -1.9739 | -2.0677
Peak drag coefficients | cFx | β (°) | [6 empty] | Peak drag coefficients | cFx | β (°)
c = 0.8 m | α (°) | 0 | 30 | 60 | 90 | 120 | 150 | 180 | c = 0.8 m | α (°) | 0 | 30 | 60 | 90 | 120 | 150 | 180
H = 0.5 m | 0 | 0.38688 | 0.32519 | 0.26162 | 0.35603 | -0.32089 | -0.27205 | -0.32032 | H = 0.5 m | 0 | 1.0019 | 1.0231 | 1.0575 | 1.0989 | -0.81701 | -0.78369 | -0.70665
U = 8.4 m/s | 15 | 0.55874 | 0.48093 | 0.27746 | 0.27289 | -0.32487 | -0.42061 | -0.46447 | U = 6 m/s | 15 | 1.6683 | 0.81912 | 1.0614 | 0.70507 | -0.52987 | -1.2526 | -1.5564
I_u = 13% | 30 | 1.4154 | 1.238 | 0.71792 | 0.31086 | -0.58776 | -1.0922 | -1.1211 | I_u = 26% | 30 | 2.5494 | 1.8756 | 1.3323 | 1.0359 | -1.3196 | -2.3875 | -2.0951
G_u = 1.44 | 45 | 1.8618 | 1.7984 | 1.1487 | 0.32971 | -1.0975 | -1.4386 | -1.3971 | G_u = 1.70 | 45 | 3.8106 | 3.0304 | 2.111 | 1.0034 | -1.4913 | -3.0098 | -2.6363
| 60 | 2.135 | 2.0084 | 1.4218 | 0.26411 | -1.2674 | -1.5495 | -1.7114 |  | 60 | 4.7883 | 3.7066 | 2.0631 | 0.5205 | -1.8103 | -3.0928 | -3.6485
| 75 | 2.253 | 2.0869 | 1.4798 | 0.31065 | -1.3824 | -1.7894 | -1.8343 |  | 75 | 4.955 | 3.9583 | 2.288 | 0.55876 | -2.5534 | -3.3705 | -4.1381
| 90 | 2.2461 | 2.0856 | 1.4936 | 0.18513 | -1.419 | -1.8836 | -2.0358 |  | 90 | 5.161 | 4.311 | 2.5188 | -0.81763 | -2.3726 | -3.6362 | -4.2709
Mean lift coefficients | cFz | β (°) | [6 empty] | Mean lift coefficients | cFz | β (°)
c = 0.8 m | α (°) | 0 | 30 | 60 | 90 | 120 | 150 | 180 | c = 0.8 m | α (°) | 0 | 30 | 60 | 90 | 120 | 150 | 180
H = 0.5 m | 0 | 0.097615 | 0.074498 | 0.034582 | 0.012337 | -0.041938 | -0.039619 | -0.083669 | H = 0.5 m | 0 | 0.3201 | 0.26944 | 0.38177 | 0.11221 | -0.11273 | -0.23274 | -0.057769
U = 8.4 m/s | 15 | 0.60146 | 0.53765 | 0.37614 | 0.062242 | -0.31384 | -0.46019 | -0.47999 | U = 6 m/s | 15 | 1.4834 | 0.48957 | 0.8047 | 0.058707 | -0.29928 | -0.44778 | -0.53659
I_u = 13% | 30 | 1.4484 | 1.217 | 0.74 | 0.042031 | -0.61723 | -1.0761 | -1.0908 | I_u = 26% | 30 | 1.8246 | 1.276 | 1.1057 | 0.083012 | -0.77667 | -1.6 | -1.4024
G_u = 1.44 | 45 | 1.2864 | 1.2496 | 0.8694 | 0.10094 | -0.90758 | -1.0616 | -0.97635 | G_u = 1.70 | 45 | 1.8403 | 1.4365 | 1.2114 | 0.078453 | -1.0044 | -1.7384 | -1.3023
| 60 | 0.96588 | 0.90723 | 0.71721 | 0.014142 | -0.66505 | -0.71837 | -0.82616 |  | 60 | 1.6865 | 1.2836 | 0.93947 | 0.014572 | -0.88587 | -0.98863 | -1.4798
| 75 | 0.52811 | 0.47117 | 0.39347 | 0.036734 | -0.35363 | -0.44407 | -0.4593 |  | 75 | 0.91412 | 0.79345 | 0.56031 | 0.014379 | -0.67331 | -0.61735 | -0.8389
| 90 | 0.14968 | 0.22042 | 0.21324 | 0.065327 | -0.18671 | -0.47963 | -0.56543 |  | 90 | 0.26323 | 0.15233 | 0.40552 | 0.11276 | -0.36035 | -0.61531 | -0.5335
Peak lift coefficients | cFz | β (°) | [6 empty] | Peak lift coefficients | cFz | β (°)
c = 0.8 m | α (°) | 0 | 30 | 60 | 90 | 120 | 150 | 180 | c = 0.8 m | α (°) | 0 | 30 | 60 | 90 | 120 | 150 | 180
H = 0.5 m | 0 | 0.48933 | 0.45132 | 0.45084 | 0.3656 | -0.41386 | -0.45669 | -0.48404 | H = 0.5 m | 0 | 1.7032 | 1.5045 | 1.9645 | 1.6446 | -1.037 | -0.87745 | -0.99244
U = 8.4 m/s | 15 | 1.1473 | 1.0702 | 0.81744 | 0.42161 | -0.68256 | -0.87827 | -0.85791 | U = 6 m/s | 15 | 3.3 | 1.8233 | 2.6332 | 1.1175 | -1.244 | -1.7915 | -2.1462
I_u = 13% | 30 | 1.886 | 1.7923 | 1.2241 | 0.38947 | -0.93504 | -1.4337 | -1.507 | I_u = 26% | 30 | 3.744 | 3.3464 | 2.9111 | 1.3987 | -2.0812 | -2.9273 | -2.5843
G_u = 1.44 | 45 | 1.7148 | 1.6835 | 1.3282 | 0.38182 | -1.1819 | -1.3524 | -1.2842 | G_u = 1.70 | 45 | 3.1691 | 3.0179 | 2.4 | 1.1733 | -1.8592 | -2.4959 | -2.1871
| 60 | 1.3191 | 1.1833 | 1.101 | 0.26239 | -0.90348 | -1.0192 | -1.0853 |  | 60 | 2.5803 | 2.0413 | 1.8551 | 0.66459 | -1.4941 | -1.6459 | -2.2176
| 75 | 0.87727 | 0.73925 | 0.65753 | 0.2559 | -0.59741 | -0.72026 | -0.72769 |  | 75 | 1.7287 | 1.3443 | 1.2969 | 0.65696 | -1.3262 | -1.2298 | -1.6178
| 90 | 0.55682 | 0.48489 | 0.44601 | 0.25417 | -0.39814 | -0.77516 | -0.86518 |  | 90 | 0.86095 | 0.8311 | 1.1897 | 1.119 | -0.96862 | -1.3069 | -1.3485
Mean hinge moment coefficients | cMHy | β (°) | [6 empty] | Mean hinge moment coefficients | cMHy | β (°)
c = 0.8 m | α (°) | 0 | 30 | 60 | 90 | 120 | 150 | 180 | c = 0.8 m | α (°) | 0 | 30 | 60 | 90 | 120 | 150 | 180
H = 0.5 m | 0 | 0.010589 | 0.0043352 | 0.0018295 | 0.0026672 | -0.0023565 | -0.0045683 | -0.0066336 | H = 0.5 m | 0 | 0.013564 | 0.008768 | 0.011113 | -0.0003871 | -0.003603 | -0.0079073 | -0.0051153
U = 8.4 m/s | 15 | 0.053326 | 0.027441 | 0.020294 | 0.0018609 | -0.038195 | -0.069588 | -0.10454 | U = 6 m/s | 15 | 0.13643 | 0.016406 | 0.019678 | -0.0014167 | -0.023465 | -0.064788 | -0.089805
I_u = 13% | 30 | 0.099274 | 0.081233 | 0.025448 | 0.0012173 | -0.045057 | -0.066266 | -0.094604 | I_u = 26% | 30 | 0.15805 | 0.064446 | 0.028538 | -0.0024351 | -0.064007 | -0.18366 | -0.16638
G_u = 1.44 | 45 | 0.045956 | 0.058934 | 0.037111 | 0.003194 | -0.046113 | -0.05028 | -0.060934 | G_u = 1.70 | 45 | 0.064915 | 0.041774 | 0.00030142 | -0.0013425 | -0.078713 | -0.094078 | -0.099762
| 60 | 0.033181 | 0.024553 | 0.015624 | 0.00036441 | -0.024169 | -0.031273 | -0.053778 |  | 60 | 0.045352 | 0.033266 | -0.021389 | -0.00050279 | -0.068732 | -0.061775 | -0.11054
| 75 | 0.017352 | 0.01697 | 0.0033078 | 0.0042483 | -0.01839 | -0.024739 | -0.022039 |  | 75 | 0.011677 | 0.0085231 | -0.026252 | -0.0014784 | -0.063644 | -0.057481 | -0.053222
| 90 | 0.011649 | 0.00096697 | -0.0001297 | -0.0051117 | -0.011981 | -0.0025164 | -0.012057 |  | 90 | 0.063654 | -0.015669 | -0.037233 | -0.010175 | -0.034876 | -0.036624 | -0.023449
Peak hinge moment coefficients | cMHy | β (°) | [6 empty] | Peak hinge moment coefficients | cMHy | β (°)
c = 0.8 m | α (°) | 0 | 30 | 60 | 90 | 120 | 150 | 180 | c = 0.8 m | α (°) | 0 | 30 | 60 | 90 | 120 | 150 | 180
H = 0.5 m | 0 | 0.10866 | 0.099929 | 0.076877 | 0.0048823 | -0.10069 | -0.10442 | -0.12611 | H = 0.5 m | 0 | 0.44548 | 0.41476 | 0.40272 | -0.0054367 | -0.049309 | -0.10166 | -0.36516
U = 8.4 m/s | 15 | 0.1408 | 0.097551 | 0.084391 | 0.0083099 | -0.15568 | -0.16844 | -0.15051 | U = 6 m/s | 15 | 0.61872 | 0.41362 | 0.51597 | -0.041965 | -0.54118 | -0.70425 | -0.76279
I_u = 13% | 30 | 0.20285 | 0.18357 | 0.1055 | 0.0074948 | -0.12191 | -0.15405 | -0.20977 | I_u = 26% | 30 | 0.65422 | 0.42955 | 0.55093 | -0.065024 | -0.52554 | -0.55597 | -0.51491
G_u = 1.44 | 45 | 0.12399 | 0.13956 | 0.12482 | 0.0087507 | -0.12382 | -0.10391 | -0.11577 | G_u = 1.70 | 45 | 0.4593 | 0.3305 | 0.41238 | -0.035564 | -0.35902 | -0.38273 | -0.39502
| 60 | 0.10049 | 0.085399 | 0.085751 | 0.0032226 | -0.081513 | -0.082866 | -0.1109 |  | 60 | 0.39781 | 0.30068 | -0.31982 | -0.033204 | -0.34504 | -0.27877 | -0.38548
| 75 | 0.08243 | 0.074154 | 0.05798 | 0.011798 | -0.069814 | -0.072308 | -0.079996 |  | 75 | 0.33884 | 0.30993 | -0.4936 | -0.072499 | -0.39532 | -0.30944 | -0.39726
| 90 | 0.039433 | 0.058395 | 0.052289 | -0.0090056 | -0.059561 | -0.059233 | -0.077535 |  | 90 | 0.20506 | -0.24478 | -0.44697 | -0.073023 | -0.3233 | -0.32667 | -0.3352
Mean overturning moment coefficients | cMy | β (°) | [6 empty] | Mean overturning moment coefficients | cMy | β (°)
c = 0.8 m | α (°) | 0 | 30 | 60 | 90 | 120 | 150 | 180 | c = 0.8 m | α (°) | 0 | 30 | 60 | 90 | 120 | 150 | 180
H = 0.5 m | 0 | 0.099848 | 0.081335 | 0.056108 | 0.049947 | -0.067535 | -0.071449 | -0.069577 | H = 0.5 m | 0 | 0.11919 | 0.085095 | 0.14717 | -0.065791 | -0.094662 | -0.098409 | -0.092765
U = 8.4 m/s | 15 | 0.27529 | 0.21047 | 0.14254 | 0.0098276 | -0.15299 | -0.25406 | -0.31916 | U = 6 m/s | 15 | 0.68024 | 0.17802 | 0.2662 | -0.0089986 | -0.12517 | -0.24256 | -0.31334
I_u = 13% | 30 | 1.0516 | 0.88454 | 0.49404 | 0.013107 | -0.45162 | -0.77822 | -0.83866 | I_u = 26% | 30 | 1.3525 | 0.89177 | 0.42222 | -0.025912 | -0.57768 | -1.2661 | -1.1331
G_u = 1.44 | 45 | 1.2906 | 1.2922 | 0.93276 | 0.053025 | -0.98309 | -1.1208 | -1.0606 | G_u = 1.70 | 45 | 1.7266 | 1.4149 | 1.189 | -0.040301 | -1.1255 | -1.7279 | -1.3892
| 60 | 1.4522 | 1.4015 | 1.198 | 0.012539 | -1.1344 | -1.1758 | -1.3256 |  | 60 | 2.1463 | 1.832 | 1.5245 | -0.013022 | -1.5255 | -1.5569 | -2.0789
| 75 | 1.5136 | 1.4368 | 1.3225 | 0.071945 | -1.2285 | -1.3861 | -1.3769 |  | 75 | 2.1501 | 2.062 | 1.8231 | -0.028014 | -2.1714 | -1.8148 | -2.1087
| 90 | -1.5306 | 1.4161 | 1.3652 | 0.029023 | -1.3179 | -1.4401 | 1.5149 |  | 90 | -2.2629 | 2.0108 | 1.922 | -0.17336 | -1.9501 | -2.0325 | -2.1052
Peak overturning moment coefficients | cMy | β (°) | [6 empty] | Peak overturning moment coefficients | cMy | β (°)
c = 0.8 m | α (°) | 0 | 30 | 60 | 90 | 120 | 150 | 180 | c = 0.8 m | α (°) | 0 | 30 | 60 | 90 | 120 | 150 | 180
H = 0.5 m | 0 | 0.42909 | 0.34532 | 0.27338 | 0.18356 | -0.3321 | -0.2834 | -0.34472 | H = 0.5 m | 0 | 1.1777 | 1.0755 | 1.1027 | -0.55163 | -0.8217 | -0.79575 | -0.98089
U = 8.4 m/s | 15 | 0.70241 | 0.55325 | 0.33618 | 0.1431 | -0.43956 | -0.5972 | -0.72784 | U = 6 m/s | 15 | 2.1685 | 0.89647 | 1.1489 | -0.36932 | -0.68115 | -1.5805 | -2.0327
I_u = 13% | 30 | 1.6279 | 1.4243 | 0.78252 | 0.16142 | -0.69317 | -1.2314 | -1.3173 | I_u = 26% | 30 | 3.1057 | 2.1112 | 1.4478 | -0.54395 | -1.5563 | -2.8877 | -2.542
G_u = 1.44 | 45 | 1.9648 | 1.9235 | 1.2353 | 0.17185 | -1.1968 | -1.5393 | -1.5175 | G_u = 1.70 | 45 | 4.0171 | 3.1557 | 2.1121 | -0.51591 | -1.734 | -3.2596 | -2.9085
| 60 | 2.206 | 2.0605 | 1.4575 | 0.13463 | -1.32 | -1.6147 | -1.8191 |  | 60 | 4.9157 | 3.8042 | 2.1347 | -0.27353 | -2.0101 | -3.2688 | -3.9335
| 75 | 2.2908 | 2.1242 | 1.4871 | 0.16476 | -1.422 | -1.8397 | -1.8792 |  | 75 | 4.9892 | 3.9834 | 2.3799 | -0.30838 | -2.7422 | -3.5401 | -4.2947
| 90 | 2.2714 | 2.0876 | 1.4939 | 0.099769 | -1.445 | -1.8888 | -2.0613 |  | 90 | 5.3338 | 4.3536 | 2.6503 | -0.43802 | -2.4823 | -3.7461 | -4.3328
Mean hinge moment coefficients | cMHx | β (°) | [6 empty] | Mean hinge moment coefficients | cMHx | β (°)
c = 0.8 m | α (°) | 0 | 30 | 60 | 90 | 120 | 150 | 180 | c = 0.8 m | α (°) | 0 | 30 | 60 | 90 | 120 | 150 | 180
H = 0.5 m | 0 | 0.010589 | 0.0043352 | 0.0018295 | 0.0026672 | -0.0023565 | -0.0045683 | -0.0066336 | H = 0.5 m | 0 | 0.013564 | 0.008768 | 0.011113 | -0.0003871 | -0.003603 | -0.0079073 | -0.0051153
U = 8.4 m/s | 15 | 0.053326 | 0.027441 | 0.020294 | 0.0018609 | -0.038195 | -0.069588 | -0.10454 | U = 6 m/s | 15 | 0.13643 | 0.016406 | 0.019678 | -0.0014167 | -0.023465 | -0.064788 | -0.089805
I_u = 13% | 30 | 0.099274 | 0.081233 | 0.025448 | 0.0012173 | -0.045057 | -0.066266 | -0.094604 | I_u = 26% | 30 | 0.15805 | 0.064446 | 0.028538 | -0.0024351 | -0.064007 | -0.18366 | -0.16638
G_u = 1.44 | 45 | 0.045956 | 0.058934 | 0.037111 | 0.003194 | -0.046113 | -0.05028 | -0.060934 | G_u = 1.70 | 45 | 0.064915 | 0.041774 | 0.00030142 | -0.0013425 | -0.078713 | -0.094078 | -0.099762
| 60 | 0.033181 | 0.024553 | 0.015624 | 0.00036441 | -0.024169 | -0.031273 | -0.053778 |  | 60 | 0.045352 | 0.033266 | -0.021389 | -0.00050279 | -0.068732 | -0.061775 | -0.11054
| 75 | 0.017352 | 0.01697 | 0.0033078 | 0.0042483 | -0.01839 | -0.024739 | -0.022039 |  | 75 | 0.011677 | 0.0085231 | -0.026252 | -0.0014784 | -0.063644 | -0.057481 | -0.053222
| 90 | 0.011649 | 0.00096697 | -0.0001297 | -0.0051117 | -0.011981 | -0.0025164 | -0.012057 |  | 90 | 0.063654 | -0.015669 | -0.037233 | -0.010175 | -0.034876 | -0.036624 | -0.023449
Peak hinge moment coefficients | cMHx | β (°) | [6 empty] | Peak hinge moment coefficients | cMHx | β (°)
c = 0.8 m | α (°) | 0 | 30 | 60 | 90 | 120 | 150 | 180 | c = 0.8 m | α (°) | 0 | 30 | 60 | 90 | 120 | 150 | 180
H = 0.5 m | 0 | 0.10866 | 0.099929 | 0.076877 | 0.0048823 | -0.10069 | -0.10442 | -0.12611 | H = 0.5 m | 0 | 0.44548 | 0.41476 | 0.40272 | -0.0054367 | -0.049309 | -0.10166 | -0.36516
U = 8.4 m/s | 15 | 0.1408 | 0.097551 | 0.084391 | 0.0083099 | -0.15568 | -0.16844 | -0.15051 | U = 6 m/s | 15 | 0.61872 | 0.41362 | 0.51597 | -0.041965 | -0.54118 | -0.70425 | -0.76279
I_u = 13% | 30 | 0.20285 | 0.18357 | 0.1055 | 0.0074948 | -0.12191 | -0.15405 | -0.20977 | I_u = 26% | 30 | 0.65422 | 0.42955 | 0.55093 | -0.065024 | -0.52554 | -0.55597 | -0.51491
G_u = 1.44 | 45 | 0.12399 | 0.13956 | 0.12482 | 0.0087507 | -0.12382 | -0.10391 | -0.11577 | G_u = 1.70 | 45 | 0.4593 | 0.3305 | 0.41238 | -0.035564 | -0.35902 | -0.38273 | -0.39502
| 60 | 0.10049 | 0.085399 | 0.085751 | 0.0032226 | -0.081513 | -0.082866 | -0.1109 |  | 60 | 0.39781 | 0.30068 | -0.31982 | -0.033204 | -0.34504 | -0.27877 | -0.38548
| 75 | 0.08243 | 0.074154 | 0.05798 | 0.011798 | -0.069814 | -0.072308 | -0.079996 |  | 75 | 0.33884 | 0.30993 | -0.4936 | -0.072499 | -0.39532 | -0.30944 | -0.39726
| 90 | 0.039433 | 0.058395 | 0.052289 | -0.0090056 | -0.059561 | -0.059233 | -0.077535 |  | 90 | 0.20506 | -0.24478 | -0.44697 | -0.073023 | -0.3233 | -0.32667 | -0.3352
Mean azimuth moment coefficients | cMz | β (°) | [6 empty] | Mean azimuth moment coefficients | cMz | β (°)
c = 0.8 m | α (°) | 0 | 30 | 60 | 90 | 120 | 150 | 180 | c = 0.8 m | α (°) | 0 | 30 | 60 | 90 | 120 | 150 | 180
H = 0.5 m | 0 | -0.0036639 | 0.00039021 | -0.0087228 | -0.0038844 | -0.026687 | 0.022263 | 0.022133 | H = 0.5 m | 0 | -0.017346 | -0.015358 | 0.029919 | 0.047529 | 0.023918 | 0.03933 | 0.05077
U = 8.4 m/s | 15 | -0.025697 | 0.020041 | 0.017855 | 0.051294 | -0.023608 | -0.023493 | 0.024408 | U = 6 m/s | 15 | 0.01841 | 0.017833 | 0.018282 | 0.012511 | -0.047843 | 0.034384 | -0.049929
I_u = 13% | 30 | 0.014543 | 0.076507 | 0.078609 | -0.0091067 | -0.13266 | -0.10396 | -0.014828 | I_u = 26% | 30 | 0.061184 | 0.13676 | 0.17893 | 0.0099957 | -0.15508 | -0.1524 | -0.041325
G_u = 1.44 | 45 | 0.0073153 | 0.11351 | 0.19711 | -0.0017825 | -0.23495 | -0.11374 | 0.0080153 | G_u = 1.70 | 45 | 0.043843 | 0.17628 | 0.2846 | 0.040011 | -0.27217 | -0.15751 | 0.029071
| 60 | 0.010877 | 0.10755 | 0.21851 | -0.0088598 | -0.21579 | -0.14637 | -6.4971e-05 |  | 60 | 0.15223 | 0.15905 | 0.31348 | -0.050985 | -0.22122 | -0.12725 | 0.011835
| 75 | 0.05206 | 0.099168 | 0.26602 | -0.038891 | -0.23897 | -0.11663 | -0.012424 |  | 75 | 0.070641 | 0.11489 | 0.42918 | -0.056093 | -0.45472 | -0.10669 | 0.027314
| 90 | 0.048655 | 0.11778 | 0.27445 | -0.015728 | -0.22353 | -0.18021 | -0.01767 |  | 90 | 0.073767 | 0.26651 | 0.51387 | -0.16941 | -0.42214 | -0.1544 | 0.132
Peak azimuth moment coefficients | cMz | β (°) | [6 empty] | Peak azimuth moment coefficients | cMz | β (°)
c = 0.8 m | α (°) | 0 | 30 | 60 | 90 | 120 | 150 | 180 | c = 0.8 m | α (°) | 0 | 30 | 60 | 90 | 120 | 150 | 180
H = 0.5 m | 0 | -0.0032421 | 0.012925 | -0.00099047 | -0.0020638 | -0.025089 | 0.033218 | 0.028932 | H = 0.5 m | 0 | -0.0020749 | 0.010055 | 0.046115 | 0.052792 | 0.023655 | 0.073196 | 0.065855
U = 8.4 m/s | 15 | -0.12361 | 0.038418 | 0.0097118 | 0.039433 | -0.030832 | -0.016778 | 0.028811 | U = 6 m/s | 15 | 0.081493 | 0.077067 | -0.070396 | -0.045477 | -0.078475 | 0.042573 | -0.049013
I_u = 13% | 30 | 0.042427 | 0.10609 | 0.2965 | -0.041026 | -0.13138 | -0.085461 | -0.012092 | I_u = 26% | 30 | 0.11845 | 0.23901 | 0.32249 | -0.15959 | -0.22638 | -0.15521 | -0.59435
G_u = 1.44 | 45 | 0.025248 | 0.14867 | 0.20666 | -0.032343 | -0.28744 | -0.11646 | -0.0037236 | G_u = 1.70 | 45 | 0.10247 | 0.33476 | 1.113 | -0.074515 | -0.82618 | -0.58204 | 0.034958
| 60 | 0.02049 | 0.1364 | 0.22646 | -0.041192 | -0.47864 | -0.15267 | 0.0030915 |  | 60 | 0.22587 | 0.33865 | 0.53857 | -0.10254 | -0.75764 | -0.57725 | -0.011386
| 75 | 0.055722 | 0.14317 | 0.37748 | -0.041096 | -0.50471 | -0.24211 | -0.026574 |  | 75 | 0.06658 | 0.28108 | 0.85507 | -0.11336 | -1.258 | -0.18918 | 0.028975
| 90 | 0.067992 | 0.29228 | 0.39149 | -0.0011846 | -0.42982 | -0.30253 | -0.022676 |  | 90 | 0.68386 | 0.73599 | 1.3637 | -0.17349 | -1.2952 | -0.17965 | 0.11072

## Design Loads
Peak velocity stow | 40 | m/s | [6 empty] | Peak velocity stow | 40 | m/s | [6 empty] | Input heliostat sizing parameters
Mean velocity stow | 27.7431 | m/s | U at H | 25.9334 | m/s |  |  |  | Mean velocity stow | 23.4714 | m/s | U at H | 20.9756 | m/s |  |  |  | Input wind characteristics
Peak velocity op | 20 | m/s | [6 empty] | Peak velocity op | 20 | m/s
Mean velocity op | 13.8715 | m/s | U at H | 12.9667 | m/s |  |  |  | Mean velocity op | 11.7357 | m/s | U at H | 10.4878 | m/s
Heliostat chord | 11 | m | [6 empty] | Heliostat chord | 11 | m
Heliostat hinge height | 5.7 | m | [6 empty] | Heliostat hinge height | 5.7 | m
Gust factor SR3 | 1.4418 |  | alpha SR3 | 0.12 |  |  |  |  | Gust factor SR4 | 1.7042 |  | alpha SR4 | 0.2
|  |  | Iu (%) | 13 | [7 empty] | Iu (%) | 26
SR3 | [8 empty] | SR4
Mean drag forces | Fx (N) | β (°) | [6 empty] | Mean drag forces | Fx (N) | β (°)
| α (°) | 0 | 30 | 60 | 90 | 120 | 150 | 180 |  | α (°) | 0 | 30 | 60 | 90 | 120 | 150 | 180
Stow design wind speed | 0 | 4047.9994 | 3632.617 | 2596.6267 | 4669.1039 | 3113.4198 | 3131.7224 | 2878.9566 | Stow design wind speed | 0 | 3114.0751 | 2270.015 | 4132.9153 | 4183.2558 | 2839.5726 | 2739.2788 | 2701.6827
Operating design wind speed | 0 | 1011.9999 | 908.1542 | 649.1567 | 1167.276 | 778.355 | 782.9306 | 719.7392 | Operating design wind speed | 0 | 778.5188 | 567.5038 | 1033.2288 | 1045.814 | 709.8932 | 684.8197 | 675.4207
| 15 | 2318.8477 | 2033.2203 | 1343.5381 | 203.5785 | 1121.5171 | 1742.1331 | 1854.1502 |  | 15 | 3688.9644 | 1211.9839 | 1874.3531 | 125.6171 | 699.7228 | 1109.1645 | 1354.7795
| 30 | 10897.9351 | 9210.7038 | 5533.6207 | 296.2112 | 4632.7421 | 8205.2002 | 8389.5917 |  | 30 | 8780.9592 | 6297.8949 | 3007.0084 | 382.726 | 3795.2738 | 7764.2625 | 6922.5822
| 45 | 14856.7099 | 14622.9265 | 10661.0322 | 1232.1356 | 11099.5901 | 12699.6299 | 11756.46 |  | 45 | 12958.7162 | 10764.7915 | 9490.6133 | 626.4943 | 7982.3597 | 12596.4702 | 9819.0063
| 60 | 17078.3819 | 16627.824 | 14318.5658 | 299.0005 | 13374.5898 | 13742.1147 | 15130.2929 |  | 60 | 16559.8056 | 14204.7546 | 11901.0264 | 201.5499 | 11304.0053 | 11643.6756 | 15188.5301
| 75 | 18137.0076 | 17206.6408 | 16078.3551 | 1673.4353 | 14636.2961 | 16436.5744 | 16377.0611 |  | 75 | 17020.6509 | 16357.303 | 14222.8404 | 428.5225 | 16526.3513 | 13757.4286 | 16159.3409
| 90 | 18455.577 | 17267.397 | 16662.4549 | 608.7159 | 15852.9965 | 17529.3886 | 18256.1522 |  | 90 | 17257.3674 | 15856.8184 | 14872.2557 | 2638.7238 | 15127.1169 | 15762.5845 | 16511.9732
Peak drag forces | Fx (N) | β (°) | [6 empty] | Peak drag forces | Fx (N) | β (°)
| α (°) | 0 | 30 | 60 | 90 | 120 | 150 | 180 |  | α (°) | 0 | 30 | 60 | 90 | 120 | 150 | 180
Stow design wind speed | 0 | 18890.0452 | 15877.9205 | 12774.1396 | 17383.6251 | 15668.1543 | 13283.4154 | 15640.2681 | Stow design wind speed | 0 | 32003.7224 | 32681.1507 | 33779.938 | 35101.3986 | 26097.205 | 25032.7028 | 22572.1076
Operating design wind speed | 0 | 4722.5113 | 3969.4801 | 3193.5349 | 4345.9063 | 3917.0386 | 3320.8538 | 3910.067 | Operating design wind speed | 0 | 8000.9306 | 8170.2877 | 8444.9845 | 8775.3496 | 6524.3013 | 6258.1757 | 5643.0269
| 15 | 6820.3735 | 5870.5665 | 3386.8375 | 3331.1302 | 3965.6057 | 5134.2307 | 5669.6589 |  | 15 | 13322.5195 | 6541.103 | 8476.2459 | 5630.3968 | 4231.32 | 10002.7146 | 12428.4232
| 30 | 17277.1587 | 15111.5439 | 8763.4088 | 3794.5253 | 7174.5783 | 13331.87 | 13685.0715 |  | 30 | 20358.7025 | 14977.4105 | 10638.8237 | 8272.0637 | 10537.9901 | 19065.8933 | 16730.326
| 45 | 22726.6226 | 21952.2896 | 14021.5613 | 4024.6012 | 13396.5027 | 17560.5062 | 17053.7821 |  | 45 | 30429.6588 | 24199.6877 | 16857.3213 | 8012.4793 | 11908.782 | 24035.3235 | 21052.5751
| 60 | 26061.5158 | 24515.4799 | 17355.1387 | 3223.9236 | 15470.9454 | 18914.5142 | 20890.5973 |  | 60 | 38237.5432 | 29599.4119 | 16475.3422 | 4156.4692 | 14456.2842 | 24697.9219 | 29135.121
| 75 | 27501.1963 | 25473.8001 | 18063.6637 | 3792.0124 | 16874.9697 | 21842.7983 | 22390.9284 |  | 75 | 39568.2728 | 31609.4942 | 18271.2929 | 4462.03 | 20390.6249 | 26915.7303 | 33045.3953
| 90 | 27417.8137 | 25458.315 | 18231.5778 | 2259.8026 | 17321.5319 | 22991.8859 | 24850.826 |  | 90 | 41213.8648 | 34426.1076 | 20114.2691 | 6529.2258 | 18946.5271 | 29037.4063 | 34105.8412
Mean lift forces | Fz (N) | β (°) | [6 empty] | Mean lift forces | Fz (N) | β (°)
| α (°) | 0 | 30 | 60 | 90 | 120 | 150 | 180 |  | α (°) | 0 | 30 | 60 | 90 | 120 | 150 | 180
Stow design wind speed | 0 | 4766.2159 | 3637.505 | 1688.5364 | 602.3716 | 2047.7077 | 1934.4846 | 4085.2789 | Stow design wind speed | 0 | 10224.6805 | 8606.4998 | 12194.6267 | 3584.3569 | 3600.9688 | 7434.2984 | 1845.2709
Operating design wind speed | 0 | 1191.554 | 909.3762 | 422.1341 | 150.5929 | 511.9269 | 483.6212 | 1021.3197 | Operating design wind speed | 0 | 2556.1701 | 2151.625 | 3048.6567 | 896.0892 | 900.2422 | 1858.5746 | 461.3177
| 15 | 7341.796 | 6562.8967 | 4591.4609 | 759.7651 | 3830.9363 | 5617.3575 | 5859.0161 |  | 15 | 11845.6398 | 3909.5097 | 6425.9649 | 468.8094 | 2389.8897 | 3575.7975 | 4284.9405
| 30 | 17679.6021 | 14856.0563 | 9032.9096 | 513.0528 | 7534.3358 | 13135.6288 | 13314.8917 |  | 30 | 14570.6615 | 10189.623 | 8829.5653 | 662.9009 | 6202.1399 | 12776.6632 | 11199.1095
| 45 | 15702.285 | 15252.9879 | 10612.4035 | 1232.1356 | 11078.4755 | 12958.9281 | 11917.9206 |  | 45 | 14696.1508 | 11471.3696 | 9673.3399 | 626.4943 | 8021.0224 | 13881.9415 | 10399.653
| 60 | 11790.1017 | 11074.1883 | 8754.7601 | 172.628 | 8118.0874 | 8768.8859 | 10084.6164 |  | 60 | 13467.8742 | 10250.2347 | 7502.2251 | 116.3649 | 7074.1922 | 7894.7541 | 11816.9922
| 75 | 6446.4978 | 5751.432 | 4802.9356 | 448.3956 | 4316.6985 | 5420.6377 | 5606.537 |  | 75 | 7299.776 | 6336.1741 | 4474.4039 | 114.8223 | 5376.7205 | 4929.8757 | 6699.1152
| 90 | 1827.1309 | 2690.5898 | 2602.9733 | 797.4221 | 2279.1221 | 5854.644 | 6902.0114 |  | 90 | 2102.0249 | 1216.4071 | 3238.2772 | 900.4189 | 2877.6182 | 4913.6215 | 4260.287
Peak lift forces | Fz (N) | β (°) | [6 empty] | Peak lift forces | Fz (N) | β (°)
| α (°) | 0 | 30 | 60 | 90 | 120 | 150 | 180 |  | α (°) | 0 | 30 | 60 | 90 | 120 | 150 | 180
Stow design wind speed | 0 | 23892.428 | 22036.3141 | 22012.9251 | 17850.7735 | 20207.4608 | 22298.7904 | 23634.1381 | Stow design wind speed | 0 | 54402.603 | 48056.2943 | 62751.4113 | 52530.9096 | 33124.7499 | 28027.8445 | 31700.692
Operating design wind speed | 0 | 5973.107 | 5509.0785 | 5503.2313 | 4462.6934 | 5051.8652 | 5574.6976 | 5908.5345 | Operating design wind speed | 0 | 13600.6507 | 12014.0736 | 15687.8528 | 13132.7274 | 8281.1875 | 7006.9611 | 7925.173
| 15 | 14004.7423 | 13063.1436 | 9978.1575 | 5146.4566 | 8331.746 | 10720.7687 | 10472.2296 |  | 15 | 26352.3514 | 14560.4467 | 21027.9262 | 8923.5649 | 9933.8148 | 14306.0375 | 17138.7281
| 30 | 23022.2633 | 21878.4978 | 14942.7075 | 4754.0982 | 11413.6538 | 17500.5136 | 18395.8458 |  | 30 | 29897.7791 | 26722.6779 | 23246.4379 | 11169.7551 | 16619.8145 | 23376.0054 | 20636.9014
| 45 | 20931.7204 | 20549.9537 | 16212.4106 | 4660.7302 | 14426.8144 | 16508.788 | 15675.8201 |  | 45 | 25307.4001 | 24099.7024 | 19165.3464 | 9369.8227 | 14846.6239 | 19931.3084 | 17465.4069
| 60 | 16101.934 | 14443.7339 | 13439.2186 | 3202.8622 | 11028.4899 | 12441.374 | 13248.3176 |  | 60 | 20604.8734 | 16301.2292 | 14813.9767 | 5307.1468 | 11931.1833 | 13143.7537 | 17708.4396
| 75 | 10708.4978 | 9023.7819 | 8026.1994 | 3123.6839 | 7292.4172 | 8792.0044 | 8882.6525 |  | 75 | 13804.794 | 10735.0954 | 10356.3941 | 5246.1567 | 10590.7298 | 9820.2965 | 12919.2657
| 90 | 6796.8574 | 5918.9341 | 5444.2447 | 3102.5335 | 4859.9966 | 9462.137 | 10560.9252 |  | 90 | 6875.192 | 6636.7603 | 9500.4503 | 8935.9732 | 7734.9782 | 10436.3409 | 10768.6626
Mean hinge moments | MHy (Nm) | β (°) | [6 empty] | Mean hinge moments | MHy (Nm) | β (°)
| α (°) | 0 | 30 | 60 | 90 | 120 | 150 | 180 |  | α (°) | 0 | 30 | 60 | 90 | 120 | 150 | 180
Stow design wind speed | 0 | 5687.1425 | 2328.3987 | 982.6057 | 1432.5316 | 1265.6598 | 2453.6251 | 3562.874 | Stow design wind speed | 0 | 4765.9789 | 3080.7633 | 3904.6013 | 136.0125 | 1265.9621 | 2778.3546 | 1797.3456
Operating design wind speed | 0 | 1421.7856 | 582.0997 | 245.6514 | 358.1329 | 316.4149 | 613.4063 | 890.7185 | Operating design wind speed | 0 | 1191.4947 | 770.1908 | 976.1503 | 34.0031 | 316.4905 | 694.5887 | 449.3364
| 15 | 7160.1994 | 3684.6442 | 2724.8901 | 249.8718 | 5128.6273 | 9343.7601 | 14036.8358 |  | 15 | 11984.221 | 1441.1334 | 1728.5437 | 124.4469 | 2061.1881 | 5691.0977 | 7888.5767
| 30 | 13329.8184 | 10907.4196 | 3416.9338 | 163.4488 | 6049.9887 | 8897.7166 | 12702.7258 |  | 30 | 13883.0061 | 5661.0328 | 2506.8164 | 213.9041 | 5622.4867 | 16132.8529 | 14615.3612
| 45 | 6170.6192 | 7913.238 | 4982.9902 | 428.8631 | 6191.7796 | 6751.289 | 8181.8387 |  | 45 | 5702.2271 | 3669.5072 | 26.4773 | 117.9294 | 6914.2215 | 8263.8928 | 8763.205
| 60 | 4455.283 | 3296.7885 | 2097.8697 | 48.9306 | 3245.2495 | 4199.1043 | 7220.988 |  | 60 | 3983.7953 | 2922.1053 | 1878.8486 | 44.1657 | 6037.5093 | 5426.3829 | 9710.3875
| 75 | 2329.8569 | 2278.5712 | 444.1523 | 570.4304 | 2469.2944 | 3321.7211 | 2959.2082 |  | 75 | 1025.7033 | 748.675 | 2305.9684 | 129.868 | 5590.5896 | 5049.192 | 4675.0863
| 90 | 1564.1421 | 129.8385 | 17.4157 | 686.3686 | 1608.6826 | 337.8783 | 1618.9828 |  | 90 | 5591.4604 | 1376.3686 | 3270.5528 | 893.7447 | 3063.5568 | 3217.0749 | 2059.8302
Peak hinge moments | MHy (Nm) | β (°) | [6 empty] | Peak hinge moments | MHy (Nm) | β (°)
| α (°) | 0 | 30 | 60 | 90 | 120 | 150 | 180 |  | α (°) | 0 | 30 | 60 | 90 | 120 | 150 | 180
Stow design wind speed | 0 | 58358.6952 | 53671.1603 | 41290.0027 | 2622.2659 | 54078.3483 | 56084.6362 | 67731.0903 | Stow design wind speed | 0 | 156524.4076 | 145731.7982 | 141502.681 | 1910.2799 | 17325.5881 | 35718.889 | 128304.5058
Operating design wind speed | 0 | 14589.6738 | 13417.7901 | 10322.5007 | 655.5665 | 13519.5871 | 14021.159 | 16932.7726 | Operating design wind speed | 0 | 39131.1019 | 36432.9496 | 35375.6703 | 477.57 | 4331.397 | 8929.7222 | 32076.1264
| 15 | 18905.5282 | 13098.4402 | 11331.4451 | 1115.7918 | 20903.2051 | 22617.4888 | 20209.8314 |  | 15 | 54348.7739 | 36332.7303 | 45323.0197 | 3686.2781 | 47538.0979 | 61862.0529 | 67004.4766
| 30 | 27237.9351 | 24648.1548 | 14166.4614 | 1006.3501 | 16368.8387 | 20685.3813 | 28166.2487 |  | 30 | 57467.1156 | 37732.4295 | 48394.3825 | 5711.7497 | 46163.7013 | 48836.9138 | 45229.9042
| 45 | 16647.9085 | 18739.315 | 16760.1003 | 1174.985 | 16625.6269 | 13952.6293 | 15544.5369 |  | 45 | 40345.7634 | 29031.9064 | 36223.9755 | 3123.9917 | 31536.3488 | 33619.7273 | 34699.3076
| 60 | 13493.0648 | 11466.746 | 11514.0799 | 432.7085 | 10945.0229 | 11126.6398 | 14891.326 |  | 60 | 34943.8686 | 26412.4566 | 28093.0542 | 2916.664 | 30308.5803 | 24487.7993 | 33861.3909
| 75 | 11068.1252 | 9956.9188 | 7785.1297 | 1584.1351 | 9374.1912 | 9709.0653 | 10741.2566 |  | 75 | 29764.457 | 27225.0331 | 43358.5348 | 6368.4303 | 34725.6522 | 27181.8114 | 34896.2168
| 90 | 5294.7693 | 7840.9272 | 7020.9463 | 1209.2086 | 7997.4374 | 7953.3417 | 10410.8916 |  | 90 | 18012.3713 | 21501.5705 | 39262.6723 | 6414.3898 | 28398.6869 | 28694.8401 | 29444.0941
Mean hinge moments | MHx (Nm) | β (°) | [6 empty] | Mean hinge moments | MHx (Nm) | β (°)
| α (°) | 0 | 30 | 60 | 90 | 120 | 150 | 180 |  | α (°) | 0 | 30 | 60 | 90 | 120 | 150 | 180
Stow design wind speed | 0 | 5687.1425 | 2328.3987 | 982.6057 | 1432.5316 | 1265.6598 | 2453.6251 | 3562.874 | Stow design wind speed | 0 | 4765.9789 | 3080.7633 | 3904.6013 | 136.0125 | 1265.9621 | 2778.3546 | 1797.3456
Operating design wind speed | 0 | 1421.7856 | 582.0997 | 245.6514 | 358.1329 | 316.4149 | 613.4063 | 890.7185 | Operating design wind speed | 0 | 1191.4947 | 770.1908 | 976.1503 | 34.0031 | 316.4905 | 694.5887 | 449.3364
| 15 | 7160.1994 | 3684.6442 | 2724.8901 | 249.8718 | 5128.6273 | 9343.7601 | 14036.8358 |  | 15 | 11984.221 | 1441.1334 | 1728.5437 | 124.4469 | 2061.1881 | 5691.0977 | 7888.5767
| 30 | 13329.8184 | 10907.4196 | 3416.9338 | 163.4488 | 6049.9887 | 8897.7166 | 12702.7258 |  | 30 | 13883.0061 | 5661.0328 | 2506.8164 | 213.9041 | 5622.4867 | 16132.8529 | 14615.3612
| 45 | 6170.6192 | 7913.238 | 4982.9902 | 428.8631 | 6191.7796 | 6751.289 | 8181.8387 |  | 45 | 5702.2271 | 3669.5072 | 26.4773 | 117.9294 | 6914.2215 | 8263.8928 | 8763.205
| 60 | 4455.283 | 3296.7885 | 2097.8697 | 48.9306 | 3245.2495 | 4199.1043 | 7220.988 |  | 60 | 3983.7953 | 2922.1053 | 1878.8486 | 44.1657 | 6037.5093 | 5426.3829 | 9710.3875
| 75 | 2329.8569 | 2278.5712 | 444.1523 | 570.4304 | 2469.2944 | 3321.7211 | 2959.2082 |  | 75 | 1025.7033 | 748.675 | 2305.9684 | 129.868 | 5590.5896 | 5049.192 | 4675.0863
| 90 | 1564.1421 | 129.8385 | 17.4157 | 686.3686 | 1608.6826 | 337.8783 | 1618.9828 |  | 90 | 5591.4604 | 1376.3686 | 3270.5528 | 893.7447 | 3063.5568 | 3217.0749 | 2059.8302
Peak hinge moments | MHx (Nm) | β (°) | [6 empty] | Peak hinge moments | MHx (Nm) | β (°)
| α (°) | 0 | 30 | 60 | 90 | 120 | 150 | 180 |  | α (°) | 0 | 30 | 60 | 90 | 120 | 150 | 180
Stow design wind speed | 0 | 58358.6952 | 53671.1603 | 41290.0027 | 2622.2659 | 54078.3483 | 56084.6362 | 67731.0903 | Stow design wind speed | 0 | 156524.4076 | 145731.7982 | 141502.681 | 1910.2799 | 17325.5881 | 35718.889 | 128304.5058
Operating design wind speed | 0 | 14589.6738 | 13417.7901 | 10322.5007 | 655.5665 | 13519.5871 | 14021.159 | 16932.7726 | Operating design wind speed | 0 | 39131.1019 | 36432.9496 | 35375.6703 | 477.57 | 4331.397 | 8929.7222 | 32076.1264
| 15 | 18905.5282 | 13098.4402 | 11331.4451 | 1115.7918 | 20903.2051 | 22617.4888 | 20209.8314 |  | 15 | 54348.7739 | 36332.7303 | 45323.0197 | 3686.2781 | 47538.0979 | 61862.0529 | 67004.4766
| 30 | 27237.9351 | 24648.1548 | 14166.4614 | 1006.3501 | 16368.8387 | 20685.3813 | 28166.2487 |  | 30 | 57467.1156 | 37732.4295 | 48394.3825 | 5711.7497 | 46163.7013 | 48836.9138 | 45229.9042
| 45 | 16647.9085 | 18739.315 | 16760.1003 | 1174.985 | 16625.6269 | 13952.6293 | 15544.5369 |  | 45 | 40345.7634 | 29031.9064 | 36223.9755 | 3123.9917 | 31536.3488 | 33619.7273 | 34699.3076
| 60 | 13493.0648 | 11466.746 | 11514.0799 | 432.7085 | 10945.0229 | 11126.6398 | 14891.326 |  | 60 | 34943.8686 | 26412.4566 | 28093.0542 | 2916.664 | 30308.5803 | 24487.7993 | 33861.3909
| 75 | 11068.1252 | 9956.9188 | 7785.1297 | 1584.1351 | 9374.1912 | 9709.0653 | 10741.2566 |  | 75 | 29764.457 | 27225.0331 | 43358.5348 | 6368.4303 | 34725.6522 | 27181.8114 | 34896.2168
| 90 | 5294.7693 | 7840.9272 | 7020.9463 | 1209.2086 | 7997.4374 | 7953.3417 | 10410.8916 |  | 90 | 18012.3713 | 21501.5705 | 39262.6723 | 6414.3898 | 28398.6869 | 28694.8401 | 29444.0941
Mean azimuth moments | Mz (Nm) | β (°) | [6 empty] | Mean azimuth moments | Mz (Nm) | β (°)
| α (°) | 0 | 30 | 60 | 90 | 120 | 150 | 180 |  | α (°) | 0 | 30 | 60 | 90 | 120 | 150 | 180
Stow design wind speed | 0 | 1967.8479 | 209.5772 | 4684.9738 | 2086.259 | 14333.6268 | 11957.5514 | 11887.2751 | Stow design wind speed | 0 | 6094.6301 | 5396.2419 | 10512.3324 | 16699.9982 | 8404.0689 | 13819.1783 | 17838.7473
Operating design wind speed | 0 | 491.962 | 52.3943 | 1171.2434 | 521.5647 | 3583.4067 | 2989.3878 | 2971.8188 | Operating design wind speed | 0 | 1523.6575 | 1349.0605 | 2628.0831 | 4174.9995 | 2101.0172 | 3454.7946 | 4459.6868
| 15 | 3450.3653 | 2690.999 | 2397.4535 | 6887.4374 | 3169.9812 | 3154.5225 | 3277.2728 |  | 15 | 1617.1928 | 1566.5132 | 1605.8716 | 1099.0224 | 4202.5991 | 3020.3683 | 4385.8463
| 30 | 1952.7687 | 10272.8074 | 10555.1356 | 1222.7852 | 17812.9757 | 13959.0548 | 1990.9673 |  | 30 | 5374.515 | 12013.3266 | 15717.8137 | 878.0343 | 13622.7104 | 13386.7961 | 3630.0101
| 45 | 982.252 | 15241.8875 | 26466.8006 | 239.3428 | 31547.3925 | 15272.7645 | 1076.241 |  | 45 | 3851.2442 | 15484.4307 | 24999.4773 | 3514.6055 | 23908.0512 | 13835.9706 | 2553.6065
| 60 | 1460.4264 | 14440.6252 | 29339.9189 | 1189.6271 | 28974.5551 | 19653.9015 | 8.7239 |  | 60 | 13372.2301 | 13971.5705 | 27536.0377 | 4478.6227 | 19431.7882 | 11177.6044 | 1039.6124
| 75 | 6990.3106 | 13315.6591 | 35718.8007 | 5222.0483 | 32087.8218 | 15660.8613 | 1668.2243 |  | 75 | 6205.2182 | 10091.6665 | 37700.0185 | 4927.2643 | 39942.8258 | 9371.3982 | 2399.3362
| 90 | 6533.0235 | 15815.2078 | 36851.1309 | 2111.8775 | 30013.4877 | 24197.2471 | 2372.6481 |  | 90 | 6479.7835 | 23410.7648 | 45139.1604 | 14880.8943 | 37081.204 | 13562.2459 | 11595.4504
Peak azimuth moments | Mz (Nm) | β (°) | [6 empty] | Peak azimuth moments | Mz (Nm) | β (°)
| α (°) | 0 | 30 | 60 | 90 | 120 | 150 | 180 |  | α (°) | 0 | 30 | 60 | 90 | 120 | 150 | 180
Stow design wind speed | 0 | 1741.3321 | 6942.167 | 531.9728 | 1108.4774 | 13474.9545 | 17840.9083 | 15539.152 | Stow design wind speed | 0 | 729.0557 | 3533.044 | 16203.016 | 18549.0772 | 8311.6476 | 25718.4656 | 23139.1333
Operating design wind speed | 0 | 435.333 | 1735.5417 | 132.9932 | 277.1194 | 3368.7386 | 4460.2271 | 3884.788 | Operating design wind speed | 0 | 182.2639 | 883.261 | 4050.754 | 4637.2693 | 2077.9119 | 6429.6164 | 5784.7833
| 15 | 16597.8818 | 5158.4871 | 1304.0368 | 5294.8581 | 4139.8569 | 2252.8216 | 3868.5822 |  | 15 | 7158.4129 | 6769.6584 | 6183.6464 | 3994.7774 | 6893.3683 | 3739.6759 | 4305.3699
| 30 | 5696.8093 | 14244.4387 | 39812.2223 | 5508.7204 | 17640.6931 | 11475.136 | 1623.614 |  | 30 | 10404.5792 | 20994.9039 | 28328.2305 | 14018.5799 | 19885.922 | 13633.8595 | 52208.8005
| 45 | 3390.0819 | 19961.7754 | 27748.7335 | 4342.7903 | 38596.0473 | 15636.8938 | 499.9805 |  | 45 | 9001.2805 | 29405.3464 | 97767.4429 | 6545.5213 | 72572.9131 | 51127.2723 | 3070.7344
| 60 | 2751.2139 | 18315.5047 | 30407.1717 | 5531.03 | 64267.9046 | 20499.2709 | 415.103 |  | 60 | 19840.3613 | 29747.1482 | 47308.9281 | 9007.0422 | 66552.2103 | 50706.4668 | 1000.1996
| 75 | 7481.9104 | 19223.8262 | 50684.8566 | 5518.1439 | 67768.8188 | 32509.1912 | 3568.2213 |  | 75 | 5848.4896 | 24690.167 | 75110.6218 | 9957.7203 | 110501.406 | 16617.5657 | 2545.1795
| 90 | 9129.5208 | 39245.2448 | 52567.2635 | 159.0655 | 57713.955 | 40621.3186 | 3044.7666 |  | 90 | 60071.307 | 64650.4799 | 119789.9302 | 15239.3819 | 113767.9543 | 15780.6743 | 9725.8539
Mean overturning moments | My (Nm) | β (°) | [6 empty] | Mean overturning moments | My (Nm) | β (°)
| α (°) | 0 | 30 | 60 | 90 | 120 | 150 | 180 |  | α (°) | 0 | 30 | 60 | 90 | 120 | 150 | 180
Stow design wind speed | 0 | 27788.7548 | 22636.371 | 15615.4415 | 13900.7956 | 18795.8401 | 19885.096 | 19363.9991 | Stow design wind speed | 0 | 21701.6577 | 15493.3186 | 26794.8869 | 11978.6625 | 17235.1616 | 17917.3979 | 16889.7546
Operating design wind speed | 0 | 6947.1887 | 5659.0928 | 3903.8604 | 3475.1989 | 4698.96 | 4971.274 | 4840.9998 | Operating design wind speed | 0 | 5425.4144 | 3873.3296 | 6698.7217 | 2994.6656 | 4308.7904 | 4479.3495 | 4222.4386
| 15 | 19153.8882 | 14644.2609 | 9917.3488 | 683.7818 | 10644.7459 | 17676.9852 | 22206.4689 |  | 15 | 30963.1057 | 8103.139 | 12116.9324 | 409.5976 | 5697.3324 | 11040.675 | 14262.5901
| 30 | 73169.8613 | 61544.254 | 34374.5867 | 911.9588 | 31422.6205 | 54146.6572 | 58352.387 |  | 30 | 61561.7414 | 40591.5118 | 19218.3263 | 1179.4422 | 26294.6133 | 57631.898 | 51576.1814
| 45 | 89799.2509 | 89911.4744 | 64899.2354 | 3689.3696 | 68401.2117 | 77985.3225 | 73795.3103 |  | 45 | 78592.3473 | 64401.6668 | 54118.4482 | 1834.396 | 51231.9686 | 78651.3983 | 63233.8293
| 60 | 101040.6117 | 97511.9343 | 83355.1499 | 872.4353 | 78925.7686 | 81811.4929 | 92229.525 |  | 60 | 97693.8206 | 83389.7922 | 69393.5865 | 592.7259 | 69438.4743 | 70867.9158 | 94625.4157
| 75 | 105312.6067 | 99966.995 | 92014.8669 | 5005.7598 | 85474.1571 | 96442.4828 | 95802.7011 |  | 75 | 97868.1115 | 93857.3465 | 82982.0478 | 1275.1253 | 98835.3095 | 82603.5824 | 95984.315
| 90 | 106493.605 | 98531.8108 | 94990.4323 | 2019.3712 | 91695.8242 | 100197.647 | 105402.3516 |  | 90 | 103002.8234 | 91524.9996 | 87483.4432 | 7890.8607 | 88764.5332 | 92513.9791 | 95826.0339
Peak overturning moments | My (Nm) | β (°) | [6 empty] | Peak overturning moments | My (Nm) | β (°)
| α (°) | 0 | 30 | 60 | 90 | 120 | 150 | 180 |  | α (°) | 0 | 30 | 60 | 90 | 120 | 150 | 180
Stow design wind speed | 0 | 119420.176 | 96106.3755 | 76084.0799 | 51087.1399 | 92428.3066 | 78872.1295 | 95940.2633 | Stow design wind speed | 0 | 214424.5433 | 195818.273 | 200773.1192 | 100434.9348 | 149607.1171 | 144883.5352 | 178590.6808
Operating design wind speed | 0 | 29855.044 | 24026.5939 | 19021.02 | 12771.785 | 23107.0767 | 19718.0324 | 23985.0658 | Operating design wind speed | 0 | 53606.1358 | 48954.5683 | 50193.2798 | 25108.7337 | 37401.7793 | 36220.8838 | 44647.6702
| 15 | 48872.558 | 38494.0557 | 23390.9674 | 9956.2676 | 30584.0015 | 41551.8571 | 50641.4393 |  | 15 | 98706.2382 | 40805.0775 | 52294.2332 | 16810.6957 | 31004.5725 | 71940.8216 | 92524.91
| 30 | 113263.5528 | 99098.6886 | 54446.0168 | 11231.5748 | 48229.2869 | 85678.8618 | 91658.091 |  | 30 | 141365.6119 | 96095.7804 | 65901.4766 | 24759.2714 | 70837.9627 | 131443.0543 | 115704.8112
| 45 | 136709.7141 | 133830.0064 | 85951.1453 | 11957.1981 | 83271.3396 | 107102.1714 | 105585.7196 |  | 45 | 182848.892 | 143641.7862 | 96138.1836 | 23483.0843 | 78928.5015 | 148370.2342 | 132389.686
| 60 | 153486.197 | 143363.6066 | 101409.1375 | 9367.5597 | 91845.1203 | 112345.2082 | 126570.61 |  | 60 | 223750.5793 | 173156.7683 | 97167.4367 | 12450.482 | 91493.1946 | 148787.9672 | 179045.8212
| 75 | 159386.8871 | 147797.9984 | 103472.6334 | 11463.9314 | 98940.9282 | 127999.5575 | 130748.4445 |  | 75 | 227096.0429 | 181314.8615 | 108325.6371 | 14036.7875 | 124817.7181 | 161139.4274 | 195484.1576
| 90 | 158042.0191 | 145254.0423 | 103940.0031 | 6941.7094 | 100537.8799 | 131421.0086 | 143423.3723 |  | 90 | 242781.9756 | 198164.6839 | 120634.6344 | 19937.8215 | 112990.5333 | 170514.33 | 197219.2787

## Critical Load Cases
[7 empty] | Input wind characteristics | [5 empty] | Peterka | Iu = 18% | [6 empty] | Peterka | Iu = 14%
[13 empty] | alpha | 0 | 15 | 30 | 45 | 60 | 90 |  | 0 | 15 | 30 | 45 | 60 | 90
[13 empty] | cFx | 0.67 | 1.18 | 2.02 | 2.93 | 3.54 | 4.05 |  | 0.06 | 0.46 | 1.22 | 1.9 | 2.41 | 2.99
[13 empty] | cFz | 0.86 | 2.03 | 2.76 | 2.49 | 2.04 | 1 |  | 0.5 | 1.03 | 1.75 | 1.67 | 1.34 | 0.26
[6 empty] | NOTES | [6 empty] | cMHy | 0.2 | 0.54 | 0.6 | 0.5 | 0.41 | 0.25 |  | 0.08 | 0.32 | 0.35 | 0.34 | 0.3 | 0.23
Maximum operating mean wind speed (m/s) |  |  |  | 12.0133 |  | *Calculated from sheet "Design Loads" | [6 empty] | cMy | 1.0184 | 2.1206 | 3.0652 | 3.801 | 4.2542 | 4.4855 |  | 0.19935 | 1.0174 | 1.8297 | 2.4923 | 2.9326 | 3.3906
Stow survival mean wind speed (m/s) |  |  |  | 24.0266 |  | *Calculated from sheet "Design Loads"
Turbulence intensity (%) |  |  |  | 18 |  | *Loads calculated from linear interpolation between data points at 13% and 26%
|  |  |  | OPERATING | [11 empty] | STOW
|  |  |  | Peak (Design) Loads |  |  |  |  | Peak Load Coefficients | [6 empty] | Peak (Design) Loads | [5 empty] | Peak Load Coefficients
Max | Iu (%) | α (°) | β (°) | Fx (N) | Fz (N) | MHy (Nm) | My (Nm) | Mz (Nm) | cFx | cFz | cMHy | cMy | cMz |  | β (°) | Fx (N) | Fz (N) | MHy (Nm) | My (Nm) | Mz (Nm) |  | cFx | cFz | cMHy | cMy | cMz
Fx | 13 | 75 | 0 | 27501.1963 | 10708.4978 | 11068.1252 | 159386.8871 | 7481.9104 | 2.253 | 0.87727 | 0.08243 | 2.2908 | 0.055722 |  | 0 | 18890.0452 | 23892.428 | 58358.6952 | 119420.176 | 1741.3321 |  | 0.38688 | 0.48933 | 0.10866 | 0.42909 | -0.0032421
Fz | 13 | 30 | 0 | 17277.1587 | 23022.2633 | 27237.9351 | 113263.5528 | 5696.8093 | 1.4154 | 1.886 | 0.20285 | 1.6279 | 0.042427 |  | 0 | 18890.0452 | 23892.428 | 58358.6952 | 119420.176 | 1741.3321 |  | 0.38688 | 0.48933 | 0.10866 | 0.42909 | -0.0032421
MHy | 13 | 30 | 180 | 13685.0715 | 18395.8458 | 28166.2487 | 91658.091 | 1623.614 | -1.1211 | -1.507 | -0.20977 | -1.3173 | -0.012092 |  | 180 | 15640.2681 | 23634.1381 | 67731.0903 | 95940.2633 | 15539.152 |  | -0.32032 | -0.48404 | -0.12611 | -0.34472 | 0.028932
My | 13 | 75 | 0 | 27501.1963 | 10708.4978 | 11068.1252 | 159386.8871 | 7481.9104 | 2.253 | 0.87727 | 0.08243 | 2.2908 | 0.055722 |  | 0 | 18890.0452 | 23892.428 | 58358.6952 | 119420.176 | 1741.3321 |  | 0.38688 | 0.48933 | 0.10866 | 0.42909 | -0.0032421
Mz | 13 | 75 | 120 | 16874.9697 | 7292.4172 | 9374.1912 | 98940.9282 | 67768.8188 | -1.3824 | -0.59741 | -0.069814 | -1.422 | -0.50471 |  | 150 | 13283.4154 | 22298.7904 | 56084.6362 | 78872.1295 | 17840.9083 |  | -0.27205 | -0.45669 | -0.10442 | 0.42909 | 0.033218
Fx | 26 | 90 | 0 | 41213.8648 | 6875.192 | 18012.3713 | 242781.9756 | 60071.307 | 5.161 | 0.86095 | 0.20506 | 5.3338 | 0.11845 |  | 90 | 35101.3986 | 52530.9096 | 1910.2799 | 100434.9348 | 18549.0772 |  | 1.0989 | 1.6446 | -0.0054367 | -0.55163 | 0.052792
Fz | 26 | 30 | 0 | 20358.7025 | 29897.7791 | 57467.1156 | 141365.6119 | 10404.5792 | 2.5494 | 3.744 | 0.65422 | 3.1057 | 0.68386 |  | 60 | 33779.938 | 62751.4113 | 141502.681 | 200773.1192 | 16203.016 |  | 1.0575 | 1.9645 | 0.40272 | 1.1027 | 0.046115
MHy | 26 | 15 | 180 | 12428.4232 | 17138.7281 | 67004.4766 | 92524.91 | 4305.3699 | -1.5564 | -2.1462 | -0.76279 | -2.0327 | -0.049013 |  | 0 | 32003.7224 | 54402.603 | 156524.4076 | 214424.5433 | 729.0557 |  | 1.0019 | 1.7032 | 0.44548 | 1.1777 | -0.0020749
My | 26 | 90 | 0 | 41213.8648 | 6875.192 | 18012.3713 | 242781.9756 | 60071.307 | 5.161 | 0.86095 | 0.20506 | 5.3338 | 0.68386 |  | 0 | 32003.7224 | 54402.603 | 156524.4076 | 214424.5433 | 729.0557 |  | 1.0019 | 1.7032 | 0.44548 | 1.1777 | -0.0020749
Mz | 26 | 90 | 60 | 20114.2691 | 9500.4503 | 39262.6723 | 120634.6344 | 119789.9302 | 2.5188 | 1.1897 | -0.44697 | 2.6503 | 1.3637 |  | 150 | 25032.7028 | 28027.8445 | 35718.889 | 144883.5352 | 25718.4656 |  | -0.78369 | -0.87745 | -0.10166 | -0.79575 | 0.073196
Fx | 18 |  |  | 32775.2996 | 9234.1494 | 13738.9891 | 191461.9211 | 27708.6014 | 3.3715 | 0.87099 | 0.12959 | 3.4612 | 0.079847 |  |  | 25125.1811 | 34907.2286 | 36647.7662 | 112118.1601 | 8205.8494 |  | 0.66073 | 0.93365 | 0.068957 | 0.47622 | 0.0223
Fz | 18 |  |  | 18462.3678 | 25666.6925 | 38864.543 | 124072.0371 | 7507.49 | 1.8516 | 2.6006 | 0.37646 | 2.1963 | 0.28913 |  |  | 24616.9271 | 38838.1908 | 90337.1513 | 150709.7695 | 7303.5182 |  | 0.64482 | 1.0567 | 0.22176 | 0.68818 | 0.019732
MHy | 18 |  |  | 13201.7452 | 17912.339 | 43104.0287 | 91991.4829 | 2655.0586 | 1.2885 | 1.7529 | 0.42247 | 1.5925 | 0.026292 |  |  | 21933.9044 | 35468.1631 | 101882.3662 | 141511.1402 | 9842.9611 |  | 0.58248 | 0.95293 | 0.24894 | 0.6651 | 0.018602
My | 18 |  |  | 32775.2996 | 9234.1494 | 13738.9891 | 191461.9211 | 27708.6014 | 3.3715 | 0.87099 | 0.12959 | 3.4612 | 0.29731 |  |  | 23933.7672 | 35627.1107 | 96114.7384 | 155960.3172 | 1351.995 |  | 0.62344 | 0.95619 | 0.2382 | 0.71702 | 0.0027932
Mz | 18 |  |  | 18120.8541 | 8141.6607 | 20869.7609 | 107284.6614 | 87776.9385 | 1.8195 | 0.82522 | 0.21488 | 1.8944 | 0.83509 |  |  | 17802.3721 | 24502.2727 | 48251.6565 | 104261.1317 | 20870.738 |  | 0.46883 | 0.61852 | 0.10336 | 0.57011 | 0.048594
|  |  |  | OPERATING | [11 empty] | STOW
|  |  |  | Mean Loads |  |  |  |  | Mean Load Coefficients | [6 empty] | Mean Loads | [5 empty] | Mean Load Coefficients
Max | Iu (%) | α (°) | β (°) | Fx (N) | Fz (N) | MHy (Nm) | My (Nm) | Mz (Nm) | cFx | cFz | cMHy | cMy | cMz |  | β (°) | Fx (N) | Fz (N) | MHy (Nm) | My (Nm) | Mz (Nm) |  | cFx | cFz | cMHy | cMy | cMz
Fx | 13 | 90 | 0 | 18455.577 | 1827.1309 | 1564.1421 | 106493.605 | 6533.0235 | 1.5119 | 0.14968 | 0.039433 | -1.5306 | 0.048655 |  | 90 | 4669.1039 | 602.3716 | 1432.5316 | 13900.7956 | 2086.259 |  | 0.095626 | 0.012337 | 0.0026672 | 0.049947 | -0.0038844
Fz | 13 | 30 | 0 | 10897.9351 | 17679.6021 | 13329.8184 | 73169.8613 | 1952.7687 | 0.89279 | 1.4484 | 0.20285 | 1.0516 | 0.014543 |  | 0 | 4047.9994 | 4766.2159 | 5687.1425 | 27788.7548 | 1967.8479 |  | 0.082906 | 0.097615 | 0.010589 | 0.099848 | -0.0036639
MHy | 13 | 15 | 180 | 1854.1502 | 5859.0161 | 14036.8358 | 22206.4689 | 3277.2728 | -0.1519 | -0.47999 | -0.15051 | -0.31916 | 0.024408 |  | 0 | 4047.9994 | 4766.2159 | 5687.1425 | 27788.7548 | 1967.8479 |  | 0.082906 | 0.097615 | 0.010589 | 0.099848 | -0.0036639
My | 13 | 90 | 0 | 18455.577 | 1827.1309 | 1564.1421 | 106493.605 | 6533.0235 | 1.5119 | 0.14968 | 0.039433 | -1.5306 | 0.048655 |  | 0 | 4047.9994 | 4766.2159 | 5687.1425 | 27788.7548 | 1967.8479 |  | 0.082906 | 0.097615 | 0.010589 | 0.099848 | -0.0036639
Mz | 13 | 90 | 60 | 16662.4549 | 2602.9733 | 17.4157 | 94990.4323 | 36851.1309 | 1.365 | 0.21324 | 0.052289 | 1.3652 | 0.27445 |  | 120 | 3113.4198 | 2047.7077 | 1265.6598 | 18795.8401 | 14333.6268 |  | -0.063765 | -0.041938 | -0.0023565 | -0.067535 | -0.026687
Fx | 26 | 90 | 0 | 17257.3674 | 2102.0249 | 5591.4604 | 103002.8234 | 6479.7835 | 2.1611 | 0.26323 | 0.20506 | -2.2629 | 0.073767 |  | 90 | 4183.2558 | 3584.3569 | 136.0125 | 11978.6625 | 16699.9982 |  | 0.13096 | 0.11221 | -0.0003871 | -0.065791 | 0.047529
Fz | 26 | 45 | 0 | 12958.7162 | 14696.1508 | 5702.2271 | 78592.3473 | 3851.2442 | 1.6228 | 1.8403 | 0.4593 | 1.7266 | 0.043843 |  | 60 | 4132.9153 | 12194.6267 | 3904.6013 | 26794.8869 | 10512.3324 |  | 0.12939 | 0.38177 | 0.011113 | 0.14717 | 0.029919
MHy | 26 | 30 | 180 | 6922.5822 | 11199.1095 | 14615.3612 | 51576.1814 | 3630.0101 | -0.86689 | -1.4024 | -0.51491 | -1.1331 | -0.041325 |  | 0 | 3114.0751 | 10224.6805 | 4765.9789 | 21701.6577 | 6094.6301 |  | 0.097491 | 0.3201 | 0.013564 | 0.11919 | -0.017346
My | 26 | 90 | 0 | 17257.3674 | 2102.0249 | 5591.4604 | 103002.8234 | 6479.7835 | 2.1611 | 0.26323 | 0.20506 | -2.2629 | 0.073767 |  | 60 | 4132.9153 | 12194.6267 | 3904.6013 | 26794.8869 | 10512.3324 |  | 0.12939 | 0.38177 | 0.011113 | 0.14717 | 0.029919
Mz | 26 | 90 | 60 | 14872.2557 | 3238.2772 | 3270.5528 | 87483.4432 | 45139.1604 | 1.8624 | 0.40552 | -0.44697 | 1.922 | 0.51387 |  | 180 | 2701.6827 | 1845.2709 | 1797.3456 | 16889.7546 | 17838.7473 |  | -0.08458 | -0.057769 | -0.0051153 | -0.092765 | 0.05077
Fx | 18 |  |  | 17994.7272 | 1932.8594 | 3113.1107 | 105150.9967 | 6512.5465 | 1.7616 | 0.19335 | 0.10313 | 1.8122 | 0.058313 |  |  | 4482.2393 | 1749.289 | 933.8704 | 13161.5136 | 7706.9279 |  | 0.10922 | 0.050751 | 0.0017902 | 0.056041 | 0.020671
Fz | 18 |  |  | 11690.5432 | 16532.1208 | 10396.1295 | 75255.4328 | 2682.9516 | 1.1735 | 1.5991 | 0.30149 | 1.3112 | 0.025812 |  |  | 4080.6594 | 7623.297 | 5001.5497 | 27406.4979 | 5254.1881 |  | 0.10078 | 0.20691 | 0.01079 | 0.11805 | 0.013762
MHy | 18 |  |  | 3803.5471 | 7912.8982 | 14259.3456 | 33502.5121 | 3412.941 | 0.42689 | 0.83477 | 0.29066 | 0.63221 | 0.030914 |  |  | 3688.7977 | 6865.6254 | 5332.8488 | 25447.5636 | 3555.0718 |  | 0.088515 | 0.18319 | 0.011733 | 0.10729 | 0.0089261
My | 18 |  |  | 17994.7272 | 1932.8594 | 3113.1107 | 105150.9967 | 6512.5465 | 1.7616 | 0.19335 | 0.10313 | 1.8122 | 0.058313 |  |  | 4080.6594 | 7623.297 | 5001.5497 | 27406.4979 | 5254.1881 |  | 0.10078 | 0.20691 | 0.01079 | 0.11805 | 0.013762
Mz | 18 |  |  | 15973.9168 | 2847.321 | 1268.6223 | 92103.1288 | 40038.8346 | 1.5563 | 0.28719 | 0.20409 | 1.5794 | 0.36653 |  |  | 2955.0594 | 1969.8474 | 1470.1543 | 18062.7303 | 15681.7501 |  | 0.071771 | 0.048027 | 0.0034176 | 0.077239 | 0.03595