## Overview
Sustainability Metrics - Overview
Version 1.0
Introduction
The University’s Sustainability Strategy 2030 – Here for Good outlines the institution’s strategic plan to address the accelerating environmental, social, economic, and human-induced climate changes occurring globally. Under the “Here for Good” commitment, the University is working towards Net Zero operational targets, with campus refurbishment and building upgrade projects playing a vital role in this initiative. Going forward, every infrastructure Capital Project must include separately estimated improvements to various relevant sustainability metrics such as energy & associated cost savings, electricity network demand savings, carbon emission abatement, water efficiency improvement, reduced waste to landfill etc. New reporting templates are now specified in the University’s updated Building Design Guidelines, under the new section “Design Standard Volume O – Sustainability Reporting Metrics.” Each tab represents specific topic. These spreadsheets must be provided by the consultant at Post Construction, however the metrics data needs to be collected during the various phases of the project.
Main Topics
PR1: Lighting
PR2: Space Heating, Cooling and Ventilation
PR3: Process Heating and Cooling
PR4: Building Envelope (BE)
PR5: Electrical (Equipment and Appliances)
PR6: On-site Renewable and Alternative Energy Initiatives
PR7: Water
Project Details |  | Colour codes
Date |  | The user needs to fill these parameters
Project Number |  | Please choose the relevant item from the dropdown menu
Project Name |  | Example (Project details)
Brief project description
Campus Name
Building Name
Baseline Calendar Year (for Pre-Project Calculations)
Instructions
Please copy the relevent fomulas from the provided example to add more projects.
You can develop your own calculations, main purpose is to capture the Pre-Project and Post-Project data according to the specified topics on the spreadsheet.
When using your own calculations, please provide details of the calculations.
UoA Proposed cost for calculations
Estimated Electricity Cost $/kWh | Estimated Electricity Demand Cost $/kVA | Estimated Gas Cost $/GJ | Estimated water Cost $/kL | Estimated LPG Cost $/litres
0.25 | 14 | 25 | 3 | 1.5
Refer below document for calculating Scope 1, 2 and 3 emissions based on the latest available emission factors provided by the Australian Government (National Greenhouse Accounts Factors)
https://www.dcceew.gov.au/climate-change/publications/national-greenhouse-accounts-factors
Below are the typical emission factors for FY 2024-25 used by UoA, Please nominate alternative emssion factor if relevant.
Table 1: Indirect (Scope 2 and Scope 3) emissions from consumption of purchased electricity from a grid
Scope 2 Emission Factors (kg CO2-e/kWh) | Scope 3 Emission Factors (kg CO2-e/kWh)
0.23 | 0.05
Table 3: Indirect (scope 2) emission factors for electricity grids
Scope 2 Emission Factors (kg CO2-e/kWh)
Off-grid | 0.67
Table 5 and Table 6: Indirect (Scope 3) emission factors for the consumption of natural gas
Scope 1 Emission Factor (kg CO2‑e/GJ) - Refer Table 5 | Scope 3 Emission Factors for Natural Gas (kg CO2-e/GJ) - Refer Table 6
51.4 | 10.7
Scope 1 Emission Factor (kg CO2‑e/GJ) - Refer Table Energy scope 1
Liquefied petroleum gas (LPG) related Emissions | 60.6
Scope 3 Emission Factors (kg CO2-e/kL)
Water related Emissions | 1.73 | Note: Sourced from the NABERS Carbon Neutral platform (specific to South Australia)
Documents Submission Stage
Upon the final design, Phase 8 (Post Construction), defined under “Design Objectives and Scope of Services”, the final data sheet should be provided, including all relevant post-project data. Data needed to be gathered during various Phases of the Project.
Note on D17: User: Please replace 'you' with 'The user needs to'

## PR1-Lighting
PR1 : Lighting
Abbreviations
ROI: Return of Investment
Note 1: Please provide the estimated costs associated with the initiative (including hardware and labour).
|  |  |  | Pre - Project | [12 empty] | Post - Project | [12 empty] | Difference (Pre and Post Project)
Initiative ID | Building Name | Location | Area m2 | Type of Activity Space | Project/Lighting Description | Control | Number of fittings | Wattage per Fitting including control gear | Estimated peak electricity load/ Peak Demand (kVA) | Estimated Energy Density W/m2 | Diversity factor (when different control methods are used) | Estimated Daily Usage Hours | Annual Days of Operation Days/yr | Annual Electricity Consumption kWh/yr | Scope 2 emissions kg CO2e | Scope 3 emissions kg CO2e | Type of Activity | Lighting Description | Control | Number of fittings | Wattage per Fitting including control gear | Estimated peak electricity load/ Peak Demand (kVA) | Estimated Energy Density W/m2 | Diversity factor (when different control methods are used) | Estimated Daily Usage Hours | Annual Days of Operation Days/yr | Annual Electricity Consumption kWh/yr | Scope 2 emissions kg CO2e | Scope 3 emissions kg CO2e | Estimated peak electricity load/ Peak Demand (kVA) | Energy Density W/m2 | Annual Energy Consumption kWh/yr | Scope 2 emissions kg CO2e | Scope 3 emissions kg CO2e
PR1.1 | Schulz | L12 | 500 | Office | 2xT8 | Manual | 100 | 68 | 7.1579 | 13.6 | 100% | 8 | 365 | 19856 | 4566.88 | 992.8 | Office | LED panel | CBUS plus Occupancy | 90 | 40 | 3.7895 | 7.2 | 75% | 8 | 365 | 7884 | 1813.32 | 394.2 | 3.3684 | 6.4 | 11972 | 2753.56 | 598.6
PR1.2 | Schulz | L10 | 500 | Meeting Room | Halogen Downlights | Manual | 10 | 65 | 0.68421 | 1.3 | 100% | 8 | 365 | 1898 | 436.54 | 94.9 | Office | LED downlights | Occupancy | 10 | 15 | 0.15789 | 0.3 | 75% | 8 | 365 | 328.5 | 75.555 | 16.425 | 0.52632 | 1 | 1569.5 | 360.985 | 78.475
PR1.3 | Schulz | External | 0 | Whole Building | Security halogen lamps | Timer | 100 | 150 | 15.7895 | N/A | 75% | 8 | 365 | 32850 | 7555.5 | 1642.5 | Common Areas | Security LED | PE cell plus timer | 100 | 50 | 5.2632 | N/A | 50% | 8 | 365 | 7300 | 1679 | 365 | 10.5263 | N/A | 25550 | 5876.5 | 1277.5
Total | [29 empty] | 14.4211 | 7.4 | 39091.5 | 8991.045 | 1954.575
Aggregated Summary
Estimated electricity saving per year (kWh / year) | Estimated Peak Demand Saving (kVA) | Total estimated Cost Saving per year ($ / year) | Scope 2 emissions kg CO2e / year | Scope 3 emissions kg CO2e / year | Total Project Cost $ Refer Note 1 | Simple Payback Yrs (if applicable) | ROI (if applicable)
39091.5 | 14.4211 | 9974.7697 | 8991.045 | 1954.575 |  | 0
mn n
Note on J7: UoA: Use appropriate power factor, in this eaxmple 0.95 power factor is used.
Note on L7: UoA: Use appropriate diversity factor, examples: Motion sensors - 50% common area corridors or 25% common area toilets, Manual control - 100%
Note on W7: UoA: Use appropriate power factor, in this eaxmple 0.95 power factor is used.
Note on Y7: UoA: Use appropriate diversity factor, examples: Motion sensors - 50% common area corridors or 25% common area toilets, Manual control - 100%

## PR2-Space HVAC
PR2: Space Heating, Cooling and Ventilation
Abbreviations
ROI: Return of Investment
Note 1: Please provide the estimated costs associated with the initiative (including hardware and labour).
|  |  |  | Pre - Project | [10 empty] | Post - Project | [10 empty] | Difference (Pre and Post Project)
Initiative ID | Building Name | Serviced section | Serviced area - m2 | Project/description | Refrigerant Type & Volume | Refrigerant Global Warming Potential | Estimated peak electricity load/ Peak Demand (kVA) | Estimated annual operating hours (hrs/year) | Estimated annual electrcity consumption kWh/yr | Estimated Annual Gas Consumption MJ/yr | Scope 1 emissions from Gas kgCO2e | Scope 3 emissions from Gas kgCO2e | Scope 2 emissions from Electricity kg CO2e | Scope 3 emissions from Electricity kg CO2e | Project/description | Refrigerant Type & Volume | Refrigerant Global Warming Potential | Estimated peak electricity load/ Peak Demand (kVA) | Estimated annual operating hours (hrs/year) | Estimated annual electrcity consumption kWh/yr | Estimated Annual Gas Consumption MJ/yr | Scope 1 emissions from Gas kgCO2e | Scope 3 emissions from Gas kgCO2e | Scope 2 emissions from Electricity kg CO2e | Scope 3 emissions from Electricity kg CO2e | Electricity load/Demand kVA | Annual Electrcity Consumption kWh/yr | Annual Gas Consumption MJ/yr | Scope 1 emissions from Gas kgCO2e | Scope 3 emissions from Gas kgCO2e | Scope 2 emissions from Electricity kg CO2e | Scope 3 emissions from Electricity kg CO2e
PR2.1 | Schulz | Whole building | 6000 | Current chiller upgrade to high efficient chiller | R22, 200L | 1810 | 240 | 2500 | 150000 | 0 | 0 | 0 | 34500 | 7500 | New Chiller | R1234ze, 250L | 7 | 180 | 365 | 100000 | 0 | 0 | 0 | 23000 | 5000 | 60 | 149635 | 0 | 0 | 0 | 11500 | 2500
PR2.2 | Schulz | Whole building | 6000 | Central Plant (as a system) | N/A | N/A | 300 | 2500 | 200000 | 75000 | 3855 | 802.5 | 46000 | 10000 | Multiple modifications & BMS tune-up | N/A | N/A | 215 | 365 | 150000 | 25000 | 1285 | 267.5 | 34500 | 7500 | 85 | 199635 | 50000 | 2570 | 535 | 11500 | 2500
Total | [25 empty] | 145 | 349270 | 50000 | 2570 | 535 | 23000 | 5000
Aggregated Summary
Estimated Annual Electrcity Saving (kWh / year) | Estimated Annual Gas Saving (GJ / year) | Estimated Peak Demand Reduction (kVA) | Estimated Annual Cost Saving ($ / year) | Scope 1 emissions kg CO2e / year | Scope 2 emissions kg CO2e / year | Scope 3 emissions kg CO2e / year | Total Project Cost $ Refer Note 1 | Simple Payback Yrs (if applicable) | ROI (if applicable)
349270 | 50 | 145 | 90597.5 | 2570 | 23000 | 5535 |  | 0
Note on J9: UoA: You can input the total annual energy consumption along with an explanation of the calculation.
Note on U9: UoA: You can input the total annual energy consumption along with an explanation of the calculation.
Note on J10: UoA: You can input the total annual energy consumption along with an explanation of the calculation.
Note on K10: UoA: You can input the total annual water consumption along with an explanation of the calculation.
Note on U10: UoA: You can input the total annual energy consumption along with an explanation of the calculation.

## PR3-Process Heating & Cooling
PR2: Process Heating, Cooling and Ventilation
Abbreviations
ROI: Return of Investment
Note 1: Please provide the estimated costs associated with the initiative (including hardware and labour).
|  |  |  | Pre - Project | [10 empty] | Post - Project | [10 empty] | Difference (Pre and Post Project)
Initiative ID | Building Name | Serviced section | Serviced area - m2 | Project/description | Refrigerant Type & Volume | Refrigerant Global Warming Potential | Estimated peak electricity load/ Peak Demand (kVA) | Estimated annual operating hours (hrs/year) | Estimated annual electrcity consumption kWh/yr | Estimated Annual Gas Consumption MJ/yr | Scope 1 emissions from Gas kgCO2e | Scope 3 emissions from Gas kgCO2e | Scope 2 emissions from Electricity kg CO2e | Scope 3 emissions from Electricity kg CO2e | Project/description | Refrigerant Type & Volume | Refrigerant Global Warming Potential | Electricity load/Demand kVA | Estimated annual operating hours (hrs/year) | Estimated annual electrcity consumption kWh/yr | Estimated Annual Gas Consumption MJ/yr | Scope 1 emissions from Gas kgCO2e | Scope 3 emissions from Gas kgCO2e | Scope 2 emissions from Electricity kg CO2e | Scope 3 emissions from Electricity kg CO2e | Electricity load/Demand kVA | Annual Electrcity Consumption kWh/yr | Annual Gas Consumption MJ/yr | Scope 1 emissions from Gas kgCO2e | Scope 3 emissions from Gas kgCO2e | Scope 2 emissions from Electricity kg CO2e | Scope 3 emissions from Electricity kg CO2e
PR2.1 | Schulz | Whole building | 6000 | Current chiller upgrade to high efficient chiller | R22, 200L | 1810 | 240 | 2500 | 150000 | 0 | 0 | 0 | 34500 | 7500 | New Chiller | R1234ze, 250L | 7 | 180 | 365 | 100000 | 0 | 0 | 0 | 23000 | 5000 | 60 | 149635 | 0 | 0 | 0 | 11500 | 2500
PR2.2 | Schulz | Whole building | 6000 | Central Plant (as a system) | N/A | N/A | 300 | 2500 | 200000 | 75000 | 3855 | 802.5 | 46000 | 10000 | Multiple modifications & BMS tune-up | N/A | N/A | 215 | 365 | 150000 | 25000 | 1285 | 267.5 | 34500 | 7500 | 85 | 199635 | 50000 | 2570 | 535 | 11500 | 2500
Total | [25 empty] | 145 | 349270 | 50000 | 2570 | 535 | 23000 | 5000
Aggregated Summary
Annual Electrcity Saving expected kWh | Annual Gas Saving expected GJ | Annual Demand Saving expected kVA | Annual Cost Saving expected $ | Scope 1 emissions kg CO2e | Scope 2 emissions kg CO2e | Scope 3 emissions kg CO2e | Total Project Cost $ Refer Note 1 | Simple Payback Yrs (if applicable) | ROI (if applicable)
349270 | 50 | 145 | 90597.5 | 2570 | 23000 | 5535 |  | 0
Note on J8: UoA: You can input the total annual energy consumption along with an explanation of the calculation.
Note on U8: UoA: You can input the total annual energy consumption along with an explanation of the calculation.
Note on J9: UoA: You can input the total annual energy consumption along with an explanation of the calculation.
Note on K9: UoA: You can input the total annual water consumption along with an explanation of the calculation.
Note on U9: UoA: You can input the total annual energy consumption along with an explanation of the calculation.

## PR4-BE
PR4: Building Envelope (BE)
Abbreviations
ROI: Return of Investment
Note 1: Please provide the estimated costs associated with the initiative (including hardware and labour).
|  |  | Pre - Project | [5 empty] | Post - Project | [5 empty] | Difference Pre and Post Project
Initiative ID | Building Name | Location | Project/description | Estimated baseline thermal load (kWh per year) | Scope 1 emissions from Gas kg CO2e | Scope 3 emissions from Gas kg CO2e | Scope 2 emissions from Electricity kg CO2e | Scope 3 emissions from Electricity kg CO2e | Project/description | Estimated improvement to Thermal load (kWh per year) | Scope 1 emissions from Gas kg CO2e | Scope 3 emissions from Gas kg CO2e | Scope 2 emissions from Electricity kg CO2e | Scope 3 emissions from Electricity kg CO2e | Annual Electricity Consumption kWh | Annual Gas Consumption MJ | Scope 1 emissions from Gas kg CO2e | Scope 3 emissions from Gas kg CO2e | Scope 2 emissions from Electricity kg CO2e | Scope 3 emissions from Electricity kg CO2e
PR3.1 | Schulz | Section xxxx | Glass windows (Western Façade) |  | 0 | 0 | 0 | 0 | High performance glass & tint (Western Façade) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PR3.2 | Schulz | Section xxxx | Roof insulation (Current) |  | 0 | 0 | 0 | 0 | Improved roof insulation |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total | [14 empty] | 0 | 0 | 0 | 0 | 0 | 0
Aggregated Summary
Estimated Annual Electricity Savings (kWh/year) | Estimated Annual Gas Savings (MJ / year) | Estimated Peak Demand Savings (kVA) | Estimated Annual Cost Saving ($ / year) | Scope 1 emissions kg CO2e | Scope 2 emissions kg CO2e | Scope 3 emissions kg CO2e | Total Project Cost $ Refer Note 1 | Simple Payback Yrs (if applicable) | ROI (if applicable)
0 | 0 | N/A | 0 | 0 | 0 | 0 |  | 0
`

## PR5-Equip
PR5: Electrical (Equipment and Appliances) - Hardwired
Abbreviations
ROI: Return of Investment
Note 1: Please provide the estimated costs associated with the initiative (including hardware and labour).
|  |  |  | Pre - Project | [14 empty] | Post - Project | [11 empty] | Difference (Pre and Post Project)
Initiative ID | Building Name | Location | Serviced Area m2 | Type of Activity Space | Project/Description | Number of devices | Equipment Size Watts | Estimated peak electricity load/ Peak Demand (VA) | Total Estimated Peak Demand kVA | Annual LPG energy Consumption (L/yr) | Annual LPG energy Consumption (GJ/yr) | Usage time per use seconds | Average number of users/day or Number of hours per day | Annual Days of Operation Days/yr | Annual Electricity Consumption kWh/yr | Scope 1 emissions from LPG kg CO2e | Scope 2 emissions from Electricity kg CO2e | Scope 3 emissions from Electricity kg CO2e | Type of Activity Space | Project/Description | Number of devices | Equipment Size Watts | Estimated peak electricity load/ Peak Demand (VA) | Estimated peak electricity load/ Peak Demand (kVA) | Usage time per use seconds | Average number of users/day or Number of hours per day | Annual Days of Operation Days/yr | Annual Electricity Consumption kWh/yr | Scope 2 emissions from Electricity kg CO2e | Scope 3 emissions from Electricity kg CO2e | Total Electricity load/Demand kVA | Annual Electricity Consumption kWh/yr | Annual LPG energy Consumption (GJ/yr) | Scope 1 emissions from LPG kg CO2e | Scope 2 emissions from Electricity kg CO2e | Scope 3 emissions from Electricity kg CO2e
PR5.1 | Schulz | L12 | 500 | Common Areas | Hand Dryer | 10 | 1200 | 13333.3333 | 13.3333 | N/A | N/A | 30 | 200 | 250 | 5000 | N/A | 1150 | 250 | Office | High efficiency hand dryer | 10 | 850 | 9444.4444 | 9.4444 | 30 | 200 | 250 | 3541.6667 | 814.5833 | 177.0833 | 3.8889 | 1458.3333 | N/A | N/A | 335.4167 | 72.9167
PR5.2 | Schulz | L12 | 500 | Dry Laboratory | Fume Cupboards | 10 | 1500 | 16666.6667 | 16.6667 | N/A | N/A | N/A | 8 | 250 | 30000 | N/A | 6900 | 1500 | Dry Laboratory | High Efficiency Fume Cupboard | 10 | 850 | 9444.4444 | 9.4444 | N/A | 8 | 250 | 17000 | 3910 | 850 | 7.2222 | 13000 | N/A | N/A | 2990 | 650
PR5.3 | Custance Area | Birks (RW011) | N/A | Residential | Instantaneous Gas Hot Water System | 1 | N/A | N/A | N/A | 32 | 1280 | N/A | N/A | N/A | N/A | 1939.2 | N/A | N/A | Residential | Heat Pump Electric Hot Water System | 1 | 3600 | N/A | N/A | N/A | N/A | N/A | 1617 | 371.91 | 80.85 | N/A | 1617 | -1280 | -1939.2 | 371.91 | 80.85
Total | [30 empty] | 11.1111 | 16075.3333 | -1280 | -1939.2 | 3697.3267 | 803.7667
Aggregated Summary
Esimated Annual Energy Saving (kWh / year) | Estimated Peak Demand Saving (kVA) | Annual LPG Saving expected GJ | Annual Cost Saving expected $ | Scope 1 emissions kg CO2e | Scope 2 emissions kg CO2e | Scope 3 emissions kg CO2e | Total Project Cost $ Refer Note 1 | Simple Payback Yrs (if applicable) | ROI (if applicable)
16075.3333 | 11.1111 | -1280 | 2254.3889 | -1939.2 | 3697.3267 | 803.7667 |  | 0
Note on I7: UoA: Use appropriate power factor, in this eaxmple 0.9 power factor is used.
Note on X7: UoA: Use appropriate power factor, in this eaxmple 0.9 power factor is used.

## PR6-Renewable
PR6: On-site Renewable and Alternative Energy Initiatives
Abbreviations
ROI: Return of Investment
Note 1: Please provide the estimated costs associated with the initiative (including hardware and labour).
|  |  | Pre - Project | [7 empty] | Post - Project | [7 empty] | Difference (Pre and Post Project)
Initiative ID | Building Name | Location | Project/description | System capacity (kW) | Estimated annual electricity generation/ consumption (kWh per year) | Estimated annual Gas energy (MJ per year) | Scope 1 emissions from Gas kg CO2e | Scope 3 emissions from Gas kg CO2e | Scope 2 emissions from Electricity avoided kg CO2e | Scope 3 emissions from Electricity avoided kg CO2e | Project/description | System capacity (kW) | Estimated annual electricity generation (kWh per year) | Estimated annual Gas energy (MJ per year) | Scope 1 emissions from Gas kgCO2e | Scope 3 emissions from Gas kgCO2e | Scope 2 emissions from Electricity avoided kg CO2e | Scope 3 emissions from Electricity avoided kg CO2e | Estimated annual electricity generation/ consumption (kWh per year) | Estimated annual Gas energy (MJ per year) | Scope 1 emissions from Gas kgCO2e | Scope 3 emissions from Gas kgCO2e | Scope 2 emissions from Electricity avoided kg CO2e | Scope 3 emissions from Electricity avoided kg CO2e
PR6.1 | Schulz | Northern Roof | None | 0 | 0 | N/A | N/A | N/A | 0 | 0 | Rooftop Solar Photovoltaics | 300 | 360000 | N/A | N/A | N/A | 82800 | 18000 | 360000 | N/A | N/A | N/A | 82800 | 18000
PR6.2 | Schulz | Northern Roof | Natural Gas | 300 | 0 | 38000 | 1953.2 | 20.8992 | 0 | 0 | Green Gas (e.g. 10% Hydrogen blended) | 300 | N/A | 38000 | 1875.072 | 20.0633 | N/A | N/A | N/A | 0 | 78.128 | 0.83597 | N/A | N/A
Total | [18 empty] | 360000 | 0 | 78.128 | 0.83597 | 82800 | 18000
Aggregated Summary | [8 empty] | `
Estimated Annual Electricity Saving (kWh/year) | Estimated Annual Gas Saving (MJ / year) | Estimated Annual Cost Saving ($/year) | Scope 1 emissions kg CO2e | Scope 2 emissions kg CO2e | Scope 3 emissions kg CO2e | Total Project Cost $ Refer Note 1 | Simple Payback Yrs (if applicable) | ROI (if applicable)
360000 | 0 | 90000 | 78.128 | 82800 | 18000.836 |  | 0
8
Note on G9: Actual figure to be calculated
Note on O9: Actual figure to be calculated
Note on P9: It is assumed that 4% emission reduction is achieved in this example, you can use appropriate value
Note on Q9: It is assumed that 4% emission reduction is achieved in this example, you can use appropriate value

## PR7-Water
PR7: Water
Abbreviations
ROI: Return of Investment
Note 1: Please provide the estimated costs associated with the initiative (including hardware and labour).
|  |  |  | Pre - Project |  |  |  |  | Post - Project |  |  |  | Difference (Pre and Post Project)
Initiative ID | Building Name | Location | Area serviced m2 | Type of Activity Space serviced by facility | Project/Description | Source of Water | Estimated Annual Water Usage kL/yr | Scope 3 emissions related to Water kgCO2e | Type of Activity Space serviced by facility | Project/Description | Estimated Annual Water Usage kL/yr | Scope 3 emissions related to Water kg CO2e | Annual Water Usage kL/yr | Scope 3 emissions related to Water kg CO2e
PR7.1 | Schulz | L12 | 500 | Common Areas | Shower head | Mains | 5000 | 8650 | Common Areas | Efficient Basin taps | 3000 | 5190 | 2000 | 3460
PR7.2 | Schulz | Whole building | 6000 | Whole Building | Cooling Tower | Mains | 75000 | 129750 | Whole Building | Efficient cooling tower | 50000 | 86500 | 25000 | 43250
Total | [12 empty] | 27000 | 46710
Aggregated Summary
Annual water Saving expected kL/yr | Annual Cost Saving expected $ | Scope 3 emissions related to Water kgCO2e | Total Project Cost $ Refer Note 1 | Simple Payback Yrs (if applicable) | ROI (if applicable)
27000 | 81000 | 46710 |  | 0
Note on H8: UoA: You can input the total annual water consumption along with an explanation of the calculation.
Note on L8: UoA: You can input the total annual water consumption along with an explanation of the calculation.
Note on H9: UoA: You can input the total annual water consumption along with an explanation of the calculation.
Note on L9: UoA: You can input the total annual water consumption along with an explanation of the calculation.

## Data Base (hidden)
Type of Activity | Type of water
Office | Mains potable water
Dry Laboratory | Mains recycled water
Wet Laboratory | Rainwater Collection
Meeting Room | Grey Water
Computer Suite
General Teaching | Renewables
Lecture Theatre | Rooftop Solar Photovoltaics
Cold Room | Biofuels for space or process heating
Common Areas | Geothermal (active/enhanced)
Whole Building | Combined Heat & Power/Cogeneration
Residential | Green hydrogen electrolysers/fuel cell
Other | Other renewable/alternative energy
Natural Gas
Green Gas (e.g. 10% Hydrogen blended)
None